## MEMO_EXTERNAL (hidden)
2020-04-06
0
0
0
Dear Mr. Al Milli:
The City of Vancouver (CoV) Neighbourhood Energy Utility (NEU) has completed a building review as per the guidelines set out in the NEU Building Connection Guidelines 2016. As per the documents submitted, the following points of confirmation have been identified. Please provide to the NEU a return letter with supporting drawings and a revised energy service application that address the points listed below.
Project Information:
Location: | 0
Developer:
Architect:
Building Mechanical Engineer: | 0
Floor Area: | 0
0
Date of Service Requested: | 0
Mechanical Specifications | Space Heating | Domestic Hot Water
|  | Summer | Winter | Reheat
Peak Demand (kW) | 0 | 0 | 0 | 0
Peak EUI (W/m2) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Annual Energy (MWh) | 0 | 0
Energy EUI (kWh/m2) | #DIV/0! | #DIV/0!
Building Side Supply T (⁰C) | asdf | 60 | 60 | 60
Building Side Return T (⁰C) | 0 | 18 | 4.4 | 0
Building Side Delta T (⁰C) | #VALUE! | 42 | 55.6 | 60
Peak Building Flow Rate (L/s) | 0 | 0 | 0 | 0
Terminal Units / DHW Storage (gal) | 0 | 0
The NEU will provide space heating and domestic hot water (DHW) to this building. The building will connect to the NEU system via two heat exchangers, one single-wall unit for heating and one double-wall unit for DHW. The NEU does not provide cooling but will consider the purchase of waste heat from buildings, provided the heat profile meets NEU needs. |  |  |  |  | put into application checklist somewhere
A. General |  |  |  | Completed
A.1 Confirm building use type(s) and associated floor area.
A.2 Provide the month of service requested.
B. Energy Profile
Space Heating
B.1 The calculated peak space heating load is 1.83 MW. This was calculated using the flow rate (39.3 L/s), specific heat capacity (4.186 kJ/kg/⁰C) and temperature differential (11.1⁰C). This is higher than the stated peak load of 600 kW. Confirm the peak space heating load.
B.2 The calculated temperature differential is 11.1⁰C. This is less than the 20⁰C required by the NEU. Increase the temperature differential to minimum 20⁰C.
B.3 The combined capacity of the two pumps for space heating is 36.6 L/s. This is less than the stated 39.3 L/s peak building flow rate. Confirm that the pumps are adequately sized.
Domestic Hot Water
B.4 Revise the return temperatures to 4.4⁰C in the winter and 18⁰C in the summer (temperature of DCW from City) and re-calculate peak loads and peak flows. Confirm that 1.4 L/s is sufficient for peak conditions. Using a temperature differential from 4.4⁰C to 60⁰C and a flow rate of 1.4 L/s, the calculated peak load should be 326 kW.
C. Heating Systems Requirements
C.1 Drawing M502 shows heating coils on heating and cooling lines as well as electric baseboards in the NEU room and the Creative Energy room. No other sources of heating are allowed as per the bylaw. Remove external heat sources or apply for an exemption justifying the requirements and include peak loads and annual demands.
C.2 NEU allows a maximum design pressure on the building side of the heat exchangers of 225 psi. Any relief valves or piping registration required by Technical Safety BC is the responsibility of the developer. Confirm building side heat exchanger design pressure and relief valve settings.
C.3 Confirm that a 35 kPa (5 psi) pressure drop is accounted for across the building side of both heat exchangers.
C.4 Pump current sensors will be required on the building space heating and DHW distribution pumps (i.e., the pumps that run water through the heat exchangers: pumps P-1A, P-1B, P-3A and P-3B) and connected to the NEU ETS control panel. Confirm that current sensors will be provided for each pump.
C.5 Confirm that combined return temperature from all heating equipment to the heat exchangers does not exceed 50⁰C in the winter and 45⁰C in the summer.
C.6 The NEU supply temperature follows a reset curve based on outside air temperature (OAT) provided in the Design Guidelines. Provide the building secondary side temperature reset curve and confirm that it complies with NEU design requirements.
C.7 Confirm that tenant improvement spaces are configured so that they can easily tie into the space heating and DHW systems and be serviced by the NEU.
D. DHW Systems Requirements
D.1 Drawing M403 shows heating coils on DHW lines. No other sources of heating are allowed as per the bylaw. Remove external heat sources or apply for an exemption justifying the requirements and include peak loads and annual demands.
D.2 Confirm that best practices will be followed to prevent scalding as per the Vancouver building by-law.
E. NEU Room Requirements
E.1 The NEU ETS room is required to be 6 m x 4 m. Confirm the dimensions of the NEU room and amount of headroom.
E.2 The doors to the NEU room are required to be at least 6' in width. It is unclear how big the doors are from the drawings provided. Provide door dimensions.
E.3 Space heating circulation pumps P-1A and P-1B and expansion tank ET-1 are located within the NEU room. Confirm that the space they occupy is not included when determining the area of the NEU room.
E.4 The floor drain is located in the centre of the NEU room. To avoid the risk of having the drain covered by the ETS skid, re-locate the NEU room floor drain to within 200 mm of a wall.
E.5 Confirm that the NEU underground pipe routing is accessible and free of obstacles. The area of penetration must be free from hoist lifts or tower cranes during construction.
F. Electrical and Controls Requirements:
F.1 Provide the electrical drawings confirming that the NEU room will have 120 V electrical service, with a lockable breaker.
F.2 Provide the electrical drawings confirming that the NEU room will have an internet connection via Ethernet with a dedicated Static IP and unique port.
F.3 Provide the drawings confirming the building will provide a 1'' dedicated conduit (with pull-string) from the mechanical room to the roof, power supply and a grounding wire for the NEU antenna at roof level.
Received Documents:
Energy Service Application | 1 Page | Not Dated
Site Plan - Plumbing (P1) | M102 | 2017-08-30
Domestic Water Riser Schematic | M403 | 2017-08-30
Level P1 - HVAC | M305 | 2017-08-30
Heating and Cooling Schematic | M503 | 2017-08-30
Equipment Schedules | M601 & M602 | 2017-08-30
If you have any questions, comments or concerns, please contact Nicole Chan at nicole.chan2@vancouver.ca or 604-873-7026.
Revision: | 0
Date: | 2020-04-06
Prepared by:
Nicole Chan, M.Sc |  | Alex Charpentier, Ph.D., P.Eng., PMP
Junior Energy Engineer |  | Senior Energy Engineer
Owner |  | Building Mechanical Engineer
Name: |  | Name:
Company: |  | Company:

## Requirements_INTERNAL (hidden)
turn this into the checklist essentially
NEU Connection Requirements
A. General | DEVELOPMENT NOTES | Comments:
1. The building is to provide building use type and floor area. | link from Application Tab
2. The building is to provide month and year of service. | link from Application Tab
B. Energy Profile
1. The building is to provide peak heating load (W/m2) and annual heating load (kWh/m2/yr) information. These metrics should align with NEU benchmarks for similar buildings built under similar codes. | checked through internal calculator
2. The building is to provide annual cooling load (kWh/m2/yr) information. These metrics are for NEU evaluation of waste heat capacity. | checked through internal calculator
3. Design temperatures must meet the temperatures required by the NEU in the document: "Building Connection Guideline". | checked through internal calculator
4. Combined return temperature from all heating equipment to the heat exchangers does not exceed 50⁰C in the winter and 45⁰C in the summer. | add to checklist, with flag
5. The building is to provide adequate pumping capacity that aligns with proposed peak flows. | already asked for a description
C. Heating Equipment Requirements
1. The maximum design pressure on the building side of the heat exchangers are 225 psi. Any relief valves or piping registration required by TSCBC is the responsibility of the developer. Confirm relief valve setpionts. | Noted in Updated Requirements. Note again in Application check list? If abve 225 psi flag - higher than ETS design.
2. A 35 kPa (5 psi) pressure drop is accounted for across the building side of both heat exchangers. | Noted in Updated Requirements. Add to check list; make then say they have accounted for 5psi
3. No other heat sources to the building other than the NEU system are allowed, as per the bylaw | Noted in Updated Requirements. Note again in Application check list? (LINK to bylaw)
4. Tenant improvement spaces must be configured so that they can easily tie into existing space heating and DHW system that are serviced by the NEU. | applicant needs to affirm this (we check there are headers)
5. The building secondary piping will not be flushed through the NEU heat exchangers. A bypass should be provided if flushing is required. | Requirements noted in Updated Guidelines. We chek there is a line for bypass in mecahnical dwg (ask dwg ref)
6.Current sensors are required on the building space heating and DHW distribution pumps that feed the heat exchangers. | ? Ask for dwg ref showing these?
6. Secondary supply temperatures will be based on outside air temperature (OAT) conditions, as outlined in the document: "Building Connection Guideline". They are to comply with NEU primary side supply and return temperatures. | added it as a check in the application /check list.
D. DHW Requirements
1. Domestic hot water is required to be run either as a instantaneous or semi instantaneous system. | in check list
2. Best practices will be followed to prevent scalding as per the Vancouver building by-law. | Noted in Updated Requirements. Note again in Application check list they have to affirm (but we don’t' check)
3. The building is to provide DHW usage sources. | ask for in check list
E. NEU Room Requirements
1. If the building is < 150,000 ft2, the minimum room size is 6 m x 3 m. Otherwise, the minimum room size is 6 m x 4 m. | asked for room size and dimension (previously confirmed at DP)
2. The NEU mechanical room has double doors at least 6' in width. | ask them to affirm.
3.The height of the room must have adequate head space. | can check through dimensions
4. The room must contain a floor drain. Not in the center of the room but within 200 mm of a wall. | can check through dimensions
5. The NEU room should be located on P1, adjacent to site of NEU DPS penetration. If another location is proposed, the Developer will be responsible for the DPS piping from the point of penetration to the location of the room. | internal
6. The DPS pipe routing must be accessible and free of obstacles. The area of penetration must be free from hoist lifts or tower cranes during construction. | ask them to affirm as part of check list
F. Electrical and Controls Requirements
2. The NEU room must have 120 V electrical service, with a lockable breaker. | applicant to affirm, dwg referehce
3. The NEU requires Internet connection via Ethernet with a dedicated Static IP and unique port. | applicant to affirm, dwg referehce
4. A 1'' dedicated conduit (with pull-string) is required from the mechanical room to the roof and a grounding wire for the antenna at roof level. | applicant to affirm, dwg referehce
5. The NEU panel requires an OAT signal from the building. | applicant to affirm, dwg referehce
6. The NEU control panel is to be located within the NEU room. | applicant to affirm, dwg referehce
Documents to be Attached: |  | Attached:
1. Energy Service Application | to be part of Excel | Y / N
2. Mechanical Schematics for Heating | requirements for full set, make refernce to location | Y / N
3. Mechanical Schematics for DHW | same | Y / N
4. Architectural Drawings showing NEU room, NEU pipe penetration location and NEU Pipe routing | same | Y / N
Y / N
5. Riser diagrams | same | Y / N
6. Monthly cooling loads | link from Application Tab | Y / N

## CALCULATOR_INTERNAL (hidden)
A. GENERAL |  |  |  |  | DEVELOPMENT NOTES |  |  |  | Questions:
Floor Area (m2) | 0 | 1 m2 = 10.769 ft2 |  |  | link from Application Tab | NEU COMMENTS |  |  | do we want them to list dwg locations for where each piece of info is.
Floor Area (ft2) | 0 | 10.769 |  |  | link from Application Tab
Building Use Type |  |  |  |  | link from Application Tab
Building Height |  |  |  |  | add to application
Missing Documents? | Y/N |  |  |  | internal check - comment only?
If Y, which ones?
B. ENERGY PROFILE | [7 empty] | LIST OF CHECKS
| Space Heat | DHW (Summer) | DHW (Winter) | DHW (Recirc.) |  | NEU COMMENTS
[6 empty] | DHW | SH
Secondary Supply Temperature (⁰C) | asdf | 60 | 60 | 60 | link from Application Tab |  |  | should be 60C for DHW
Secondary Return Temperature (⁰C) | 0 | 18 | 4.4 | 0 | link from Application Tab |  |  | DHW summer should be 18C, winter should be 4.4C
Secondary Flow Rate (L/s) | 0 | 0 | 0 | 0 | link from Application Tab
Peak Load (MW) | 0 | 0 | 0 | 0 | link from Application Tab
Delta T (⁰C) | #VALUE! | 42 | 55.6 | 60 | internal calc |  |  | Space Heating delta T should be < 20
| Space Heat (MWh) | DHW (MWh)
January | 0 | 0 |  |  | link from Application Tab
February | 0 | 0 |  |  | link from Application Tab
March | 0 | 0 |  |  | link from Application Tab
April | 0 | 0 |  |  | link from Application Tab
May | 0 | 0 |  |  | link from Application Tab
June | 0 | 0 |  |  | link from Application Tab
July | 0 | 0 |  |  | link from Application Tab
August | 0 | 0 |  |  | link from Application Tab
September | 0 | 0 |  |  | link from Application Tab
October | 0 | 0 |  |  | link from Application Tab
November | 0 | 0 |  |  | link from Application Tab
December | 0 | 0 |  |  | link from Application Tab
Total | 0 | 0 |  |  | internal calc |  |  | Compare with reported Totals
CALCULATOR
Calculated Load (MW) | #VALUE! | 0 | 0 | 0 | based on MCDeltaT
Difference in Load | #VALUE! | 0 | 0 | 0 | show this calc; different should be 0=mcDeltaT; numbers are…wrong (see comments); show stopper |  |  | Compare with calculated values (WARNING: MOSTLY RESIDENTIAL)
Peak EUI (W/m2) | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | show calc; seems atypical flag; if above ?? Then showstopper (ask NC) |  |  | Heating EUI should be less than 45 W/m2 and DHW EUI should be less than 35 W/m2
Total Peak EUI | #DIV/0! |  |  |  | show calc which ttotals both
Energy EUI (kWh/m2) | #DIV/0! | #DIV/0! |  |  | show as info only. If high, then 'seems other high' |  |  | Heating EUI should be less than 60 kWh/m2 and DHW EUI should be less than 50 kWh/m2
Total Energy EUI | #DIV/0! |  |  |  | show only.
Cooling Loads:
Cooling (MWh)
January | 0 |  |  |  | link from Application Tab
February | 0 |  |  |  | link from Application Tab
March | 0 |  |  |  | link from Application Tab
April | 0 |  |  |  | link from Application Tab
May | 0 |  |  |  | link from Application Tab
June | 0 |  |  |  | link from Application Tab
July | 0 |  |  |  | link from Application Tab
August | 0 |  |  |  | link from Application Tab
September | 0 |  |  |  | link from Application Tab
October | 0 |  |  |  | link from Application Tab
November | 0 |  |  |  | link from Application Tab
December | 0 |  |  |  | link from Application Tab
Total | 0 |  |  |  | internal calc; don't show
Can NEU use their waste heat? | Y/N |  |  |  | ?internal evaluation only? Don't show.
C. HEATING EQUIPMENT REQUIREMENTS
NEU COMMENTS
Space Heating:
Configuration Checked | Y / N |  |  |  | intneral review only, don't show or ask applicatnt to fill out
Type of Heating Equipment: |  |  |  |  | application asks for description, NEU checks
Building Side Pressure (kPa) |  |  |  |  | Applicant to fill out; specify dwg
Inlet Temperature |  |  |  |  | internal check to look at secondary system temperatures and whether they match NEU supplies; multiple pieces of equipment; ask them to specify which drawing this is found in
Outlet Temperature |  |  |  |  | same
Appropriate Reset Schedule? | Y / N |  |  |  | add into application; add calculator for curve. |  |  | showstopper
Number of Pumps |  |  |  |  | applicant fill out, specify dwg
Pump Names |  |  |  |  | create a table for pumps (room for 8)
Flow per Pump (L/s) |  |  |  |  | same as above
Sized Correctly? | Y / N |  |  |  | internal calc but more info provided by application re: pumps and strategy |  |  | ask about pumping strategy in the application
Location Checked? | Y / N |  |  |  | internal check only
General Comments: |  |  |  |  | internal check only
D. DHW REQUIREMENTS
NEU COMMENTS
DHW:
Type of configuration |  |  |  |  | options: instantaneous or semi-; other with option
Number of Storage Tanks |  |  |  |  | fill out and reference dwg (6)
Size of Tanks (gallons) |  |  |  |  | fill out and reference dwg
Total Storage (gallons) |  |  |  |  | fill out and reference dwg
DHW end users |  |  |  |  | hot tub, kitchen, pool - applicant to fill out in a box.
Building Side Pressure (kPa) |  |  |  |  | Applicant to fill out; specify dwg
Number of Pumps |  |  |  |  | applicant fill out, specify dwg
Pump Names |  |  |  |  | create a table for pumps (room for 8)
Flow per Pump (L/s) |  |  |  |  | same as above
Sized Correctly? | Y / N |  |  |  | internal calc but more info provided by application re: pumps and strategy
Location Checked? | Y / N |  |  |  | internal check only
General Comments |  |  |  |  | internal check only
E. NEU ROOM REQUIREMENTS
NEU COMMENTS
Is the room near DPS penetration? | Y / N |  |  |  | internal (NEU room dwg) (with dimensions of the room include height, or show dimensions on dwgs)
Can the room access accomodat ethe skid? | Y/N |  |  |  | internal check
Is the DPS connection technically sound? | Y / N | only if > 20 m is stress analysis req. |  |  | internal check
Are the dimensions sufficient? | Y / N |  |  |  | see above
Is floor drain location OK? | Y / N |  |  |  | internal check for distance from wall 200mm
Do the doors meet our requirements? | Y / N |  |  |  | internal check
check for other heat sources (as per bylaw)

## Appl+Checklist
Application for Thermal Energy Service |  |  |  |  | INTERNAL Development Notes | COLOUR LEGEND | Dropdown options
Complete this Application to initiate the NEU Connectivity Review. Fill in grey cells only. The NEU Connectivity Review must be finalized prior to issuance of the Building Permit. Refer to the Neighbourhod Energy Utility Connectivity Guidelines and Requirements for details. Submit this Application as a PDF with signatures and as an Excel file. | [5 empty] | not editable by applicant | Yes | Yes
A: Property Information | [5 empty] | Fill in by Applicant | No | No
Municipal Address: | [6 empty] | Unknown | Not applicable
Building Permit No.: |  | Application Date:
Total Building Floor Area (m2): |  | Gross heated floor area only
Residential Floor Area (m2): |  | Other Floor Area Type: |  |  |  |  | Check OK
Commercial Floor Area (m2): |  | Other Floor Area (m2): |  |  |  |  | OK
Industrial Floor Area (m2): |  | Other Floor Area Type:
Institutional Floor Area (m2): |  | Other Floor Area (m2):
How many buildings are requesting service as part of this Application? |  | Building Height (m):
Number of Storeys (above grade): |  | Number of Parkade levels:
B: Billing/Owner Information
Name:
Contact:
Address:
Postal Code:
Telephone:
Email:
C: Mechanical/HVAC Designer Information
Mechanical/HVAC Designer: |  | Energy Modeller:
Contact Person: |  | Contact Person:
Address: |  | Address:
Telephone: |  | Telephone:
Email: |  | Email:
D: Service & Billing Information
Site Availablity for Service Connection (DD-MMM-YYYY): |  | Notes: - The date of service request marks the date when the building will require heat/hot water and when billing will begin, regardless of building occupancy. -The date of service request may be revised to if more than six months' notice is provided to NEU Engineer. It is the responsibility of the Developer to express any desired change to the service request date prior to the six month from the initial service request date. - For information on NEU billing refer to http://vancouver.ca/neu
Date of Service Requested (DD-MMM-YYYY):
Date of Occupancy (DD-MMM-YYYY):
E: Building Energy Usage
E.1 Building Energy System Parameters
| Space Heating | Domestic Hot Water (Summer) | Domestic Hot Water (Winter) | Domestic Hot Water (Recirc)
System Supply Temperature (°C): | asdf | 60 | 60 | 60
System Return Temperature (°C): |  | 18 | 4.4
Temperature Differential (°C): | 0 | 42 | 55.6 | 0
Check for Temperature Differential - Space Heating: |  |  |  |  | Need to work on check formulas
System Flowrate (L/s):
Peak Load (MW):
Calculated Peak Loads (MW): | 0 | 0 | 0
Coincident Peak Load (MW):
Check for Estimated Peak Load - Space Heating: |  |  |  |  | Need to work on check formulas
Check for Estimated Peak Load - DHW Summer: |  |  |  |  | Need to work on check formulas
Check for Estimated Peak Load - DHW Winter: |  |  |  |  | Need to work on check formulas
Check for Peak EUI - Space Heating (W/m2): | 0 |  |  |  | Heating EUI should be less than 45 W/m2 and
Need to work on check formulas
Check for Peak EUI - DHW (W/m2): | 0 |  |  |  | DHW EUI (max of either Winter or Summer) should be less than 35 W/m2 (derek said check this value?)
Need to work on check formulas
FOR NEU ENTRY ONLY Approved Coincident Peak Load (MW): |  | Note: For Rate Class 2 and 3 customers, billing of monthly levy charge will be based on the peak load value approved by the NEU Engineer at the completion of the NEU Connectivity Review. Refer to Energy Utility System By-law No. 9552 for details. |  |  | (internal entry for fixed capacity levy.
E.2 Monthly Usage Estimates
Monthly Energy Requirements (MWh) | Space Heating | Domestic Hot Water | Cooling (if any)
January
February
March
April
May
June
July
August
September
October
November
December
Total | 0 | 0 | 0
Note: In some instances, the NEU piping network may accept waste heat from building cooling systems. Please contact the NEU staff at the earliest opportunity to discuss feasibility.
Check for EUI - Space Heating (kWh/m2): |  | EUI value is higher than typical residential development, please confirm. |  |  | Heating EUI should be less than 60 kWh/m2 | don’t check if blank - done
Check for EUI - DHW (kWh/m2): |  | EUI value is higher than typical residential development, please confirm. |  |  | DHW EUI should be less than 50 kWh/m2 | don’t check if blank - done
E.3 Energy Submetering
Will the building be submetered for energy consumed downstream of the NEU meter? |  |  |  |  | Y/N/Unknown Options
If yes, provide name of submetering company: |  |  |  |  | for information only
F: Detailed Design Information
F.1: Space Heating System Details
Provide a short description of each connected building's space heating system:
For example: Building A is heated by hot water radiators in commercial and residential suites; common and amenity spaces are heated by fan coils and ventilation AHUs. Building B residential units are heated by convectors and radiant flooring; common and amenity areas are heated by fan coils and ventilation AHUs.
Space Heating System Reset Parameters:
Outdoor Ambient Temperature | Space Heating System Supply Temperature (°C): | Notes:
-7 (°C): |  |  |  |  | <45, >70 red flag
7 (°C): |  |  |  |  | <50, >60 red flag
15 (°C): |  |  |  |  | <45,>50 red flag
Note: refer to Figure 4 of the NEU Connectivity Guidelines and Requirements document for recommended heating system supply temperatures. The Guidelines are found here: https://vancouver.ca/files/cov/neigbourhood-energy-utility-connectivity-guidelines-requirements.pdf
Space Heating System Details:
Note: List the temperature values for each heating system separately where available. For example, fan coils, AHUs, radiators/convectors, radiant flooring, etc. If additional columns are needed, please provide details on a separate page.
| System 1 | System 2 | System 3 | System 4
Heating System Type: |  |  |  |  | internal check to look at secondary system temperatures and whether they match NEU supplies; multiple pieces of equipment
Inlet Temperature (°C):
Outlet Temperature (°C):
Drawing Reference:
Confirm that the combined return temperature from all heating equipment to the NEU heat exchanger does not exceed 50°C in the winter and 45°C in the summer.
Maximum Heating System Pressure at the inlet of ETS heat exchanger (kPa):
Confirm that a 35 kPa (5 psi) pressure drop is accounted for across the building side of the space heating heat exchanger.
Space Heating System Pumps:
Number of pumps in heating system:
Provide a short description of the space heating system's pumping strategy:
For example: Space heating system consists of 3 pumps; each is sized for 50% of load.
Provide the following information for each pump in space heating system: | Pump Name | Pump Flow (L/s) | Pump Location (Drawing Reference)
Heating Pump 1
Heating Pump 2
Heating Pump 3
Heating Pump 4
Heating Pump 5
Heating Pump 6
Heating Pump 7
Heating Pump 8
Note: If additional rows are needed, please provide details on a separate page.
F.2: Domestic Hot Water Heating System Details
Provide a short description of each connected building's domestic hot water heating system:
Example system types: instantaneous, semi-instanteous, storage DHW.
Number of storage tanks: |  | Drawing reference:
Size of tanks (m3) |  | Total storage (m3)
Please list any atypical uses of domestic hot water in the building(s):
Examples may include: hot tubs, pools, landscaping or water features, commercial or industrial applications, etc.
Maximum DHW system pressure at the inlet of ETS heat exchanger (kPa):
Confirm that a 35 kPa (5 psi) pressure drop is accounted for across the building side of the DHW heat exchanger.
DHW System Pumps:
Number of pumps in DHW system:
Provide a short description of the DHW system's pumping strategy:
For example: Domestic hot water systems for buildings A and B are served by 3 pumps, each sized for 50% of load.
Provide detailed information for each pump in domestic hot water heating system: | Pump Name | Pump Flow (L/s) | Pump Location (Drawing Reference) |  | internal calc but more info provided by application re: pumps and strategy
DHW Pump 1 |  |  |  |  | internal check only
DHW Pump 2
DHW Pump 3
DHW Pump 4
DHW Pump 5
DHW Pump 6
DHW Pump 7
DHW Pump 8
Note: If additional rows are needed, please provide details on a separate page.
G: Application Checklist
The Applicant is to acknowledge and confirm that the following requirements are met. Refer to the NEU Connectivity Guidelines and Requirements for further details.
G.1 ETS Room Requirements
ETS Room Area (m2): |  |  |  |  | applicant enter data
Which drawing shows the ETS Room location? |  |  |  |  | drawing location
Are the ETS Room dimensions shown on the relevant drawing? |  |  |  |  | Y/N only; if NO, make red
Which drawing shows the entry point of the NEU distribution piping into the building? |  |  |  |  | drawing location
Is the ETS Room kept clear of other equipment? |  |  |  |  | Y/N only; if NO, make red
Has the ETS Room been provided with a floor drain? |  |  |  |  | Y/N only; if NO, make red
Is the floor drain located 200mm from a wall (and not in the centre of the room)? |  |  |  |  | Y/N only; if NO, make red
Is the ETS Room door a double-door with zero clearance entry, with minimum 1.83m height? |  |  |  |  | Y/N only; if NO, make red
Have adequate flood protection been provided to the ETS room as per the relevant building code requirements? |  |  |  |  | y/n/not applicable
For any questions answered with 'No' above, please provide explanation: |  |  |  |  | ask applicant to explain No
G.2 NEU Connectivity Requirements
If the building mechanical system incorporates any heat production equipment, as allowed by the Energy Utility System By-Law No. 9552, provide a list indicating: equipment type; power capacity in kW; and location within the building.
Has the ETS Room been provided with a single dedicated 120V, 15A circuit with lockable breaker for connection to the NEU Panel? |  |  |  |  | Y/N only; if NO, make red
Which drawing shows the above electrical requirements? |  |  |  |  | drawing location
Have the following communications requirements been provided:
-1" dedicated conduit (with string) from rooftop to ETS Room? |  |  |  |  | Y/N only; if NO, make red
-dedicated 15A 110 V circuit at rooftop to supply antenna, with grounding wire at rooftop? |  |  |  |  | Y/N only; if NO, make red
-internet connection via Ethernet with a dedicated Static IP and unique port? |  |  |  |  | Y/N only; if NO, make red
Which drawing shows the above communications requirements? |  |  |  |  | drawing location
Have signals from current sensors (indicating pump status) on the building space heating and DHW distribution pumps been provided to the NEU Panel? |  |  |  |  | Y/N only; if NO, make red
Which drawing shows the above controls requirements? |  |  |  |  | drawing location
Has a dedicated outdoor air temperature (OAT) signal been provided to the NEU Panel? |  |  |  |  | Y/N only; if NO, make red
Which drawing shows the OAT signal to the NEU Panel? |  |  |  |  | drawing location
Does the design of the building's DHW systems implement anti-scalding best practices as per relevant Code requirements? |  |  |  |  | Y/N only; if NO, make red
Have tenant improvement spaces to be fit up in the future been configured so they can easily integrate into existing space heating and DHW systems serviced by the NEU? |  |  |  |  | Y/N/ not applicable only; if NO, make red
Which drawing shows mechanical systems connections for future tenant improvement areas? |  |  |  |  | drawing location
Have arrangements been made to ensure the NEU distribution piping route is kept accessible and free of obstacles during construction? |  |  |  |  | Y/N only; if NO, make red
For any questions answered with 'No' above, please provide explanation: |  |  |  |  | ask applicant to explain No
G.3 NEU Service Requirements
Does the design allow the ETS heat exchangers to be bypassed by spool pieces during the flushing of the building's hot water systems? |  |  |  |  | Y/N only
Which drawing shows the heat exchanger bypass? |  |  |  |  | drawing location
For any questions answered with 'No' above, please provide explanation: |  |  |  |  | ask applicant to explain No
H. Submission Requirements
Have the following documentation been submitted as part of this Application?
Full set of Mechanical Drawings, including the following (as PDF submitted as part of a single ZIP file): - schematics for DHW and HVAC and controls - plumbing and electrical equipment schedules - riser diagrams |  |  |  |  | Y/N only; if NO, make red
Full architectural drawing set in PDF format |  |  |  |  | Y/N only; if NO, make red
CAD files for the floor plan of the ETS Room |  |  |  |  | Y/N only; if NO, make red
For any questions answered with 'No' above, please provide explanation: |  |  |  |  | ask applicant to explain No
I: Acceptance on behalf of the Owner
I certify that the information I have provided on this Application is correct. |  |  |  |  | some statement about being true to best knowledge
Applicant Signature:
Applicant Name:
Date:
Phone #:
Note: Electronic signatures are acceptable. Submit this Application as a PDF with signatures and as an Excel file. |  |  |  |  | NEU signs final version only
Application for Thermal Energy Service - version 2 - April 6, 2020

## Version History
Version # | Version Release Date | Notes
1 |  | PDF application form
2 | April 6 2020 | Updated to Excel format