## Intro, Info & Instructions
Alterations to Existing NECB&ZEBP Buildings - Energy Requirements
Applicability
This checklist is to be completed when performaing alterations to existing buildings subject to Clause 11.7.1.1.(3)(b) of Vancouver's Building By-law. This clause generally applies to buildings containing commercial (Office, Retail), or buildings over 3 storeys containing multifamily dwellings. This checklist is to also be used when altering buildings originally designed to any version of NECB.
This checklist supports the alteration requirements when applying the "Alterations Language to Support the Application of the NECB 2015" found online within the Notes to Part 11 section of Vancouver's Building By-law, but first, follow the steps below to see if your project can be exempted from the energy checklist documentation process.
STEP 1: Review the applicability of the energy process to your project
IMPORTANT Energy Checklist Process: Applicability
Some project types do not need to complete the energy checklist process. Projects where the entire scope of work is limited to that listed on the Energy Checklist Exemption form are exempt from the energy checklist and submission process.
How to apply for an exemption from the energy checklist process: Projects eligible for the energy checklist exemption can submit a completed Energy Checklist Exemption form found within the "Energy Requirements for Tenant Improvements" document (link below). Simply print out the exemption form and indicate the applicable project type(s). Include a hardcopy of the completed exemption form with your building permit application package.
IMPORTANT: Applying the Energy Checklist Exemption to an ineligible project will result in the building permit application being rejected on the basis of insufficient energy documentation.
Any project where the scope of work involves energy components of the building's systems, such as building envelope insulation, exterior doors or glazing/skylights, motors (>1 HP), burners, coils, heat exchangers, transformers, receptacles, lights, and/or controls for HVAC/Lighting/Service Water Heating systems, is required to complete the energy checklist and submission process.
Access the Energy Checklist Exemption form (within the Energy Requirements for Tenant Improvements document)
STEP 2: Review the Training Videos on how to use and apply the energy checklist and documentation
Tutorials: Training Videos
In January 2016, the City of Vancouver began providing web-based training videos to assist applicants with the energy checklists needed for building permit applications. These training videos are accessible via the following link:
Access the energy checklist Training Videos
STEP 3: Review the details for submission of energy documentation
Submission Format and Process
Effective June 3, 2019, this Alterations checklist is to be submitted at the Permit application stage. Submit online with your Building Permit application.
The content of this submission is to reflect the scope of work only, and not the base building equipment or envelope characteristics.
Occupancy Permit Application Stage
Complete the Occupancy Permit portion of the same energy checklist finalized during the building permit stage, then submit with your occupancy permit application.
Check the appropriate box that confirms whether or not the building permit stage energy checklist still accurately reflects the completed project. If not, then indicate this and resubmit the appropriate energy compliance forms needed to update the energy documents for this project. Resubmit only the forms needed to accurately reflect the changes made during the construction phase.
STEP 4: As needed, review detailed information to assist with the completion of the energy documentation
The following information is meant to supplement the information provided in the training videos. It is meant to be referenced, as needed, if additional information is necessary. We strongly recommend the training videos be viewed prior to reviewing the following detailed information.
Alterations to Existing Buildings
Use the "Energy Checklist for Alterations to Existing Buildings" when the following two conditions apply;
| i) | the project space has been previously occupied, and
| ii) | the scope of work includes one or more of the following classifications: Repair, Minor Renovation, Major Renovation, Reconstruction, Additions, Changes of Major Occupancy Classification
(Note: For "Additions" projects, this checklist is to be used in conjunction with the New Construction energy checklist in the event the original building is being altered to accomodate the addition.)
Permit applications for "alteration" projects are to report their energy compliance with;
| i) | Section 11.7 of Part 11 |  | of the VBBL, and
| ii) | the | "Alteration Language Supporting the Application of NECB" |  |  |  |  | within the Notes to Part 11.
Completing the Checklist for Alterations to Existing Buildings
Review the training videos - link provided above.
At the bottom of this screen there are a number of excel tabs. The next tab is the "Energy Checklist - Alterations" and is to be completed and submitted for building permit. Note that there are several other tabs that show samples of various completed checklists. Be sure to follow these samples carefully to minimize the chance of delaying your permit application. It is important to note that checklists with blanks will be considered incomplete and the applicant will be asked to resubmit.
The checklist is divided into three parts;
|  | i) | General building data meant to provide information relevant to building energy performance,
|  | ii) | Energy requirements of the VBBL's Part 10 which references the NECB energy standards/code, and
|  | iii) | Energy upgrade requirements of the VBBL's Part 11 |  |  |  | (Ends effective Jan 1, 2023 for all new applications.)
The content of this submission is to reflect the project's scope of work only, and not the base building equipment or envelope characteristics.
Specific information about how to apply and complete the energy sections can be found below.
General Building Data
Provide information about the building and project. Review the Samples (see tabs at bottom of screen) and complete the building and/or tenancy address information as per the samples.
Indicate all applicable Categories of Alterations triggered by the scope of work. Indicate the Use of the space or spaces, and their respective areas. Indicate the building's status with respect to Neighbourhood Energy (N/E) systems.
Category of Alteration (shown as "Indicate all that apply")
There are a number of alteration categories. The final category applied to a project is always based on the scope of work and/or space use classification.
Alterations projects typically include some level of construction. Change of Major Occupancy Classification projects do not necessarily involve construction. Regardless, all building permit applications are assessed on scope of work and changes to Major Occupancy classification. The intake staff will assist with this determination, although this information can also be found within Vancouver's Building By-law.
If unsure, then use the following as a guide:
Voluntary Upgrade: This is the voluntary upgrade of a building's energy component such as replacing a boiler with a more efficient boiler, or any piece of an HVAC system with a more efficient piece or system, or lighting with more efficient lighting. It is important to note that any and all work performed on the building's envelope is always defined as Voluntary Upgrade. Voluntary Upgrade is not an exemption under the Part 11 Energy Upgrade Mechanism, however, it is an alteration that does not trigger additional upgrade requirements.
Minor Renovation: (Most alterations projects fall into this category.) This is the alteration of non-energy components, such as interior walls or floors, within a single suite/tenancy, or multiple suites/tenancies that are being consolidated into a single suite/tenancy.
Major Renovation: This is the alteration of non-energy components, such as interior walls or floors, within a single suite/tenancy, or multiple suites/tenancies that will result in multiple suites/tenancies.
Change of Major Occupancy Classification: This scenario is a significant change of use that has a multitude of implications pertaining to the building, electrical, and fire codes. Issues might include changes to occupancy levels and/or hazard levels etc. as well as trigger required changes to lighting power levels.
Space Use, Area & Performance Information
Most alterations projects are limited to a single space with a single space use such as office or retail, however some alterations projects involve a single space with multiple uses such as an office or retail in front with a workshop or warehouse or storage space or spaces in back. Some alterations projects will involve more than one space, sometimes on more than one floor. Indicate as many different space uses as is relevant to the project. Note that the "Building Use Description" tool is available if unsure about how to categorize a particular space and its use.
Indicate the area of each space listed in square meters. Also, indicate the total area of all spaces involved in the alteration project, when grouped as;
|  | - | "Non-residential Conditioned Space": |  |  | Spaces pertaining to Commercial, Retail, Industrial, Institutional uses etc.
|  | - | "Residential Conditioned Space": |  |  | Common areas in residential buildings including building envelope work of residential suites
|  | - | "Semiheated Space": |  |  | Spaces not fully "conditioned". Typically storage areas or work garages with overhead doors that are often opened or left open. Basically, not designed to maintain 22C.
(Note that the term "Conditioned" is meant to indicate "heated" and/or "air-conditioned" and suitable for continuous occupancy, as opposed to semiheated storage spaces not meant to be occupied.)
Building Entrance(s): Indicate if the space is accessed directly from the outdoors and whether or not the scope of work includes alterations to an existing outdoor entrance, or the creation of a new outdoor entrance.
Neighbourhood Energy (N/E) Systems
(Neighbourhood energy systems are energy supply systems such as the steam system in Gastown that supplies heat to buildings typically through below grade tie-in and heat exchanger systems)
First, if the building is within a N/E area then use the drop-down to indicate which system, otherwise indicate "N/A" if not within a N/E area. Next, indicate if the building is actually connected to the N/E system as some buildings are not connected. Answering these two questions will automatically result in the "TI's thermal energy requirement" being indicated in the last box. For instance, it may forbid the use of electric water heaters to be installed as the building may already provide stub-outs for heat exchanger type water heaters.
Energy Requirements: VBBL Part 10 & NECB 2015/ZEBP (10.2.2.5)
Part 10 of the VBBL references energy requirements in the form of standards (90.1/NECB/ZEBP) or individual requirements such as Articles 10.2.2.8 through 10.2.2.22.
10.2.2.22 is an allowance for limited exterior heating of patios for Food and Beverage establishments only. It has a number of requirements pertaining to type of heating and associated controls to prevent heating of unoccupied spaces and heating during warm weather conditions.
NECB/ZEBP energy requirements for alterations projects are dependent upon the scope of work. The energy-related scope of work is determined through the following applicability process for the following areas;
Applying the NECB/ZEBP Energy Requirements for Alterations to Existing Buildings
Within the Notes to Part 11, the "Alteration Language Supporting the Application of NECB" document outlines the requirements for alterations work in the energy related areas of Building Envelope, HVAC, Service Water Heating, Power, and Lighting. The following can be used to determine if NECB energy requirements apply based on the project's scope of work in these areas.
Building Envelope applies…
… if your scope of work on the building envelope includes the addition or deletion of glazing, skylights, doors, or insulation.
IMPORTANT: All Building Envelope work is automatically considered "Voluntary Upgrade". This can be indicated on row 12 and on rows 76-78 of the checklist.
HVAC applies…
… if you are adding any HVAC equipment (including kitchen exhaust and make-up air systems) that has an energy component such as motors (greater than 1 HP), burners, coils, or heat exchangers.
Service Water Heating applies…
… if you are adding any Service Water Heating equipment (boilers, hot water heater, on-demand system) that has an energy component such as motors (greater than 1 HP), burners, coils, or heat exchangers.
Power applies…
… if you are adding new Transformers or new Receptacles.
Lighting applies…
… if you are adding lighting, and/or
… if you are replacing or removing lighting load to a space.
Steps:
| i) | Determine which sections apply and indicate on the checklist.
| ii) | Indicate the responsible party for each section.
| iii) | Review the Sample tabs and complete each section accordingly.
| iv) | Use the links (blue underlined) within each section to access the "Alteration Language Supporting the Application of NECB" document. Complete only the documents within the sections that apply to the project. Refer to the sample documents, where provided.
Energy Statements on Drawings
This criteria does not apply to Part 11 TI projects.
The Energy Upgrade Mechanism ends effective Jan 1, 2023 for all new applications.
See "Sample - Energy Statements" (green tab) at the bottom of your screen. Within the "Tools and Reference Materials" section of the energy web page, download the "Energy Statements on Drawings" excel tool. (Note: for smaller projects, this information can be written on the drawings by hand)
|  |  | Energy Webpage: |  | http://vancouver.ca/building-energy-requirements
The purpose of this statement process is to provide a simple yet accurate way of determining the energy design criteria used in a building's original design, and subsequent upgrades. Energy statements on the drawings will provide a foundation upon which future design teams can assess building performance and determine the most effective approach to achieve their energy upgrade goals.
Effective January 1, 2015, the City of Vancouver's new Building By-law requires existing buildings to perform some form of energy upgrade/assessment when applying for building permits. Design teams will need historical energy design information in order to provide the best assessment for energy upgrades. Archive drawings with clear and concise energy design criteria will provide valuable assistance to future design teams.

## Validation Reference (hidden)
|  | Climate Zone |  | City | Zone
Yes |  | Zone 4 < 3000 HDD | 2 |  |  | Type of Building
No |  | Zone 5 3000 to 3999 HDD | 3 |  |  | New
N/A |  | Zone 6 4000 to 4999 HDD | 4 |  |  | Addition to existing building
|  | Zone 7A 5000 to 5999 HDD | 5
|  | Zone 7B 6000 to 6999 HDD | 6
|  | Zone 8 ≥ 7000 HDD | 7 |  |  | Building Area Method
Space-by-Space Method
Help Messages
Message 1 | Certain NECB requirements are climatic zone dependant. Please refer to Table C-1 for to find the number of heating degree-days (HDD) for your building location and enter the number of HDDs for your building location. If the building is semi-heated select the appropriate value from the 'Degree-Days Below 15C' column and enter the value under the "Heating Degree Days 15C" field.
Message 2 | A building with a design set-point temperature less that 15C is considered to be 'semi-heated'.
Message 3 | For additional information on calculating building envelope areas, please refer to Article 3.1.1.6.
Split system
Single-package system
Air conditioners, all electric phases, split and single-package
Heat pumps, split and single package
SPVAC and SPVHP in cooling mode
SPVHP in heating mode
Evaporatively cooled
Evaporatively cooled and water evaporatively cooled, split and single-package
Water evaporatively cooled air conditioners, split and single-package
Air-cooled and water evaporatively cooled
Air-cooled
Water evaporatively cooled
Ground-source and water-source heat pumps
Internal water-loop heat pumps
Water-cooled air conditioners
Direct-expansion ground-source heat pumps
PTAC
PTHP in cooling mode
PTHP in heating mode
Room air conditioners with reverse cycle
with louvered sides
without louvered sides
Room air conditioners without reverse cycle
Room air conditioners with louvered sides, with reverse cycle
Room air conditioners without louvered sides
Room air conditioner heat pumps with louvered sides
Room air conditioner heat pumps without louvered sides
Room air conditioner, casement only
Room air conditioner, casement slider
Air conditioners, air-cooled
Air conditioners, water-cooled
Air conditioners, water-cooled with fluid economizer
Air conditioners, glycol-cooled
Air conditioners, glycol-cooled with fluid economizer
Chilled water air handler
Vapour compression, air- or water-cooled, electrically operated
Absorption, single- or double-effect, indirect-
or direct-fired
Electric boilers
Gas-fired boilers
Oil-fired boilers (No. 2 oil)
Oil-fired boilers, residual (No. 5 or No. 6 oil) and other oils
Gas-fired warm-air furnaces
Gas-fired duct furnace
Gas-fired unit heater
Gas-fired outdoor packaged units
Oil-fired warm-air furnace
Oil-fired duct furnaceand unit heaters
Cooling tower - centrifugal fan, direct-contact
Cooling tower - propeller or axial fan, direct-contact
Cooling tower - centrifugal fan, indirect-contact evaporative
Cooling tower - propeller or axial fan, indirect-contact evaporative
Condenser - centrifugal, indirect-contact evaporative
Condenser - propeller or axial fan, indirect-contact evaporative
Condenser - air cooled

## Code Tables (hidden)
Part 3
| Table 3.2.2.2. | [32 empty] | Table 3.2.2.4. | [7 empty] | Table 3.2.3.1
| Above Ground Opaque Building Assembly | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 |  | Component | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 | [18 empty] | Component |  | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 | Assemblies in Contact with the Ground | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000
| Wall | 0.315 | 0.278 | 0.247 | 0.21 | 0.21 | 0.183 |  | Fenestration | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6 | [18 empty] | All Doors |  | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6 | Walls | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Roof | 0.227 | 0.183 | 0.183 | 0.162 | 0.162 | 0.142 | [34 empty] | Roofs | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Floor | 0.227 | 0.183 | 0.183 | 0.162 | 0.162 | 0.142 | [34 empty] | Floors | 0.757 | 0.757 | 0.757 | 0.757 | 0.757 | 0.379
| Fenestration | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6
| Doors | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6
| Underground Walls | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Underground Roofs | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Underground Floors | 0.757 | 0.757 | 0.757 | 0.757 | 0.757 | 0.379
| FDWR Requirements Article 3.2.1.4. | [14 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
| Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 |  | Lighting Power Density by Building Type for Use with the Building Area Method (Forming Part of Sentences 4.2.1.5.(1), (4) and (5)) | [7 empty] | 1: Table 6.2.2.1.; 4: SL (top inlet); 6: SL (bottom inlet); 8: SL (top inlet); 10: SL (bottom inlet); 12: SL (w division); 14: EF; 15: Et (& instant); 16: Et and SL (w Q & sq root Vr) combo; 19: UEF (w FHR and Vs)
1 | 0.4 | 0.4 | 0.47 | 0.47 | 0.47 | 0.2 |  | Building Type | Lighting Power Density, W/m2 | [5 empty] | 1 | 1: Electric, storage-type; Input ≤ 12 kW; Capacity 50 ≤ Vr < 270 L; 2: SL ≤ 40 + 0.20Vr (bottom inlet); SL ≤ 35 + 0.20Vr (top inlet); 3: SL ≤ SL ≤; 4: 35; 5: 0.2; 6: 40; 7: 0.2; 21: SL = SL =
[8 empty] | Automotive facility | 8.1 | [5 empty] | 2 | 1: Electric, storage-type; Input ≤ 12 kW; Capacity 270 ≤ Vr < 454 L; 2: SL ≤ 0.472Vr - 33.5 (bottom inlet); SL ≤ 0.472Vr - 38.5 (top inlet); 3: SL ≤ SL ≤; 8: 0.472; 9: 38.5; 10: 0.472; 11: 33.5; 21: SL = SL =
[8 empty] | Convention centre | 6.9 | [5 empty] | 3 | 1: Electric, storage-type; Input > 12 kW; ΔT = 44.4°C; 2: SL ≤ 0.3 +102.2/Vr; 3: SL ≤; 12: 0.3; 13: 102.2; 21: SL =
[8 empty] | Courthouse | 8.5 | [5 empty] | 4 | 1: Electric, storage-type, heat pump; Input ≤ 24A and ≤ 250 V; 2: EF ≥ 2.1; 3: EF ≥; 14: 2.1; 21: EF =
[8 empty] | Dining: bar lounge/leisure | 8.6 | [5 empty] | 5 | 1: Electric, instantaneous;; 2: typically approaches 100% efficiency; 3: Et ≥; 15: 98; 21: Et =
[8 empty] | Dining: cafeteria/fast food | 8.2 | [5 empty] | 6 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; FHR < 68; 2: UEF ≥ 0.3456 - (0.00053 Vs); 3: UEF ≥; 19: 0.3456; 20: 0.00053; 21: UEF =
[8 empty] | dining: family | 7.6 | [5 empty] | 7 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; 68 ≤ FHR < 193; 2: UEF ≥ 0.5982 - (0.00050 Vs); 3: UEF ≥; 19: 0.5982; 20: 0.0005; 21: UEF =
[8 empty] | Dormitory | 5.7 | [5 empty] | 8 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; 193 ≤ FHR < 284; 2: UEF ≥ 0.6483 - (0.00045 Vs); 3: UEF ≥; 19: 0.6483; 20: 0.00045; 21: UEF =
[8 empty] | Exercise centre | 7.8 | [5 empty] | 9 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; FHR ≥ 284; 2: UEF ≥ 0.6920 - (0.00034 Vs); 3: UEF ≥; 19: 0.692; 20: 0.00034; 21: UEF =
[8 empty] | Fire station | 6 | [5 empty] | 10 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; FHR < 68; 2: UEF ≥ 0.6470 - (0.00016 Vs); 3: UEF ≥; 19: 0.647; 20: 0.00016; 21: UEF =
[8 empty] | Gymnasium | 8.2 | [5 empty] | 11 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; 68 ≤ FHR < 193; 2: UEF ≥ 0.7689 - (0.00013 Vs); 3: UEF ≥; 19: 0.7689; 20: 0.00013; 21: UEF =
[8 empty] | Health care clinic | 8.7 | [5 empty] | 12 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; 193 ≤ FHR < 284; 2: UEF ≥ 0.7897 - (0.00011 Vs); 3: UEF ≥; 19: 0.7897; 20: 0.00011; 21: UEF =
[8 empty] | Hospital | 10.3 | [5 empty] | 13 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; FHR ≥ 284; 2: UEF ≥ 0.8072 - (0.00008 Vs); 3: UEF ≥; 19: 0.8072; 20: 8e-05; 21: UEF =
[8 empty] | Hotel/Motel | 6 | [5 empty] | 14 | 1: Gas-fired, storage type; 22 kW < Input ≤ 30.5 kW; Capacity Vr ≤ 454 L; FHR > 0; 2: UEF ≥ 0.8107 - (0.00021 Vs); 3: UEF ≥; 19: 0.8107; 20: 0.00021; 21: UEF =
[8 empty] | Library | 8.9 | [5 empty] | 15 | 1: Gas-fired, storage type; All other Input Powers; ΔT = 50°C; 2: Et ≥ 78% SL ≤ (1.25 Q) + (16.57 √Vr); 3: Et ≥ SL ≤; 16: 78; 17: 1.25; 18: 16.57; 21: Et = SL =
[8 empty] | Manufacturing facility | 8.8 | [5 empty] | 16 | 1: Gas-fired, instant's; < 59 kW; Capacity Vr ≤ 7.6 L; Input/Vs ≥ 310 W/L; < 6.4 L/min; 2: UEF ≥ 0.86; 3: UEF ≥; 19: 0.86; 20: 0; 21: UEF =
[8 empty] | Motion picture theatre | 4.7 | [5 empty] | 17 | 1: Gas-fired, instant's; < 59 kW; Capacity Vr ≤ 7.6 L; Input/Vs ≥ 310 W/L; ≥ 6.4 L/min; 2: UEF ≥ 0.87; 3: UEF ≥; 19: 0.87; 20: 0; 21: UEF =
[8 empty] | Multi-unit residential building | 4.8 | [5 empty] | 18 | 1: Gas-fired, instantaneous; All other Input Powers; Input/Vs ≥ 310 W/L; 2: Et ≥ 94%; 3: Et ≥; 15: 94; 21: Et =
[8 empty] | Museum | 5.9 | [5 empty] | 19 | 1: Solar Thermal Service Water Heaters; Electric back-up; All Capacities; 2: SEF ≥ 1.4; 3: SEF ≥; 14: 1.4; 21: SEF =
[8 empty] | Office | 6.9 | [5 empty] | 20 | 1: Solar Thermal Service Water Heaters; Gas-fired back-up; All Capacities; 2: SEF ≥ 0.9; 3: SEF ≥; 14: 0.9; 21: SEF =
[8 empty] | Penitentiary | 7.4 | [5 empty] | 21 | 1: Pool Heaters, gas-fired; Input < 117.2 kW; 2: Et ≥ 82%; 3: Et ≥; 15: 82; 21: Et =
[8 empty] | Performing arts theatre | 9 | [5 empty] | 22 | 1: Pool Heaters, oil-fired; 2: Et ≥ 78%; 3: Et ≥; 15: 78; 21: Et =
[8 empty] | Police station | 7.1 | [5 empty] | 23 | 1: Pool Heaters, heat pump; Outdoor air 10°C db / 6.8°C wb; 26.7°C entering water; 2: ≥ 4.0 COP; 3: COP ≥; 15: 4.0 COP; 21: COP =
[8 empty] | Post office | 7 | [5 empty] | 24 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; 2: EF ≥ 0.68 - (0.0005 Vr); 3: EF ≥; 19: 0.68; 20: 0.0005; 21: EF =
[8 empty] | Religious building | 7.2 | [5 empty] | 25 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; FHR < 68; 2: UEF ≥ 0.2509 - (0.00032 Vs); 3: UEF ≥; 19: 0.2509; 20: 0.00032; 21: UEF =
[8 empty] | Retail area | 9 | [5 empty] | 26 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; 68 ≤ FHR < 193; 2: UEF ≥ 0.5330 - (0.00042 Vs); 3: UEF ≥; 19: 0.533; 20: 0.00042; 21: UEF =
[8 empty] | School/university | 7.8 | [5 empty] | 27 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; 193 ≤ FHR < 284; 2: UEF ≥ 0.6078 - (0.00042 Vs); 3: UEF ≥; 19: 0.6078; 20: 0.00042; 21: UEF =
[8 empty] | Sports arena | 8.2 | [5 empty] | 28 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr ≤ 76 L; FHR ≥ 284; 2: UEF ≥ 0.6815 - (0.00037 Vs); 3: UEF ≥; 19: 0.6815; 20: 0.00037; 21: UEF =
[8 empty] | Storage garage | 1.9 | [5 empty] | 29 | 1: Oil-fired, storage type; 30.5 kW< Input ≤ 41 kW; Vr ≤ 454 L; Input/Vs < 310 W/L; FHR > 0; 2: UEF ≥ 0.6740 - (0.00035 Vs); 3: UEF ≥; 19: 0.674; 20: 0.00035; 21: UEF =
[8 empty] | Town hall | 7.4 | [5 empty] | 30 | 1: Oil-fired, storage type; All other Input Powers; 2: Et ≥ 80% SL ≤ (1.25 Q) + (16.57 √Vr); 3: Et ≥ SL ≤; 16: 80; 17: 1.25; 18: 16.57; 21: Et = SL =
[8 empty] | Transportation facility | 5.4 | [5 empty] | 31 | 1: Oil-fired, instantaneous; Input ≤ 61.5 kW; 2: EF ≥ 0.59 - (0.0005 Vr); 3: EF ≥; 19: 0.59; 20: 0.0005; 21: EF =
[8 empty] | Warehouse | 4.8 | [5 empty] | 32 | 1: Oil-fired, instant's; Input Others; Vr < 37.8 L; Input/Vs ≥ 310 W/L; 2: Et ≥ 80%; 3: Et ≥; 15: 80; 21: Et =
[8 empty] | Workshop | 9.8 | [5 empty] | 33 | 1: Oil-fired, instant's; Input Others; Vr ≥ 37.8 L; Input/Vs ≥ 310 W/L; ΔT = 50°C; 2: Et ≥ 78% SL ≤ (1.25 Q) + (16.57 √Vr); 3: Et ≥ SL ≤; 16: 78; 17: 1.25; 18: 16.57; 21: Et = SL =
Lighting Power Density by Space Type for Use with Space by Space Method | bar: 1 to 2
[8 empty] | Space Type | Lighting Power Density, W/m2
[8 empty] | Atrium < 6 m in height | 4.2 |  |  | Component or Equipment | Cooling or Heating Capacity, kW (Btu/h) | Standard | Rating Conditions(1) | 1: Minimum Performance(2)
[8 empty] | Atrium between 6 m and 12 m in height | 5.2 |  |  | Split system | < 19 (65 000) | CSA C656 | — | 1: SEER = 15(3)
[8 empty] | Atrium > 12 m in height | 6.5 |  |  | Single-package system | < 19 (65 000) | CSA C656 |  | 1: SEER = 14(3)
[8 empty] | Audience seating area – permanent for auditorium | 6.5 |  |  | Air conditioners, all electric phases, split and single-package | ≥ 19 (65 000) and | CAN/CSA-C746 | ≥ 19 kW and < 40 kW, electric resistance heating section or no heating section | 1: COP = 3.28(3)
[8 empty] | Audience seating area – permanent for gymnasium | 2.5 |  |  |  | < 223 (760 000) |  |  | 1: ICOP = 3.34
[8 empty] | Audience seating area – permanent for motion picture theatre | 2.9 |  |  | Heat pumps, split and single package |  |  | ≥ 19 kW and < 40 kW, non-electric heating section | 1: COP = 3.22(3)
[8 empty] | Audience seating area – permanent for penitentiary | 7.2 |  |  | SPVAC and SPVHP in cooling mode |  |  |  | 1: ICOP = 3.28
[8 empty] | Audience seating area – permanent for performing arts theatre | 12.5 |  |  | SPVHP in heating mode |  |  | ≥ 40 kW and < 70 kW, electric resistance heating section or no heating section | 1: COP = 3.22(3)
[8 empty] | Audience seating area – permanent for religious building | 7.8 |  |  | Evaporatively cooled |  |  |  | 1: ICOP = 3.28
[8 empty] | Audience seating area – permanent for sports arena | 3.5 |  |  | Evaporatively cooled and water evaporatively cooled, split and single-package |  |  | ≥ 40 kW and < 70 kW, non-electric heating section | 1: COP = 3.17(3)
[8 empty] | Audience seating area – permanent other | 2.5 |  |  | Water evaporatively cooled air conditioners, split and single-package |  |  |  | 1: ICOP = 3.22
[8 empty] | Banking activity area and offices | 6.5 |  |  | Air-cooled and water evaporatively cooled |  |  | ≥ 70 kW and < 223 kW, electric resistance heating section or no heating section | 1: COP = 2.93(3)
[8 empty] | Classroom/Lecture hall/Training room for penitentiary | 9.5 |  |  | Air-cooled |  |  |  | 1: ICOP = 2.96
[8 empty] | Classroom/Lecture hall/Training room other | 7.6 |  |  | Water evaporatively cooled |  |  | ≥ 70 kW and < 223 kW, non-electric heating section | 1: COP = 2.87(3)
[8 empty] | Computer/Server room | 10.1 |  |  | Ground-source and water-source heat pumps |  |  |  | 1: ICOP = 2.90
[8 empty] | Conference/Meeting/ Multi-purpose room | 10.5 |  |  | Internal water-loop heat pumps | ≥ 223 (760 000) |  | ≥ 223 kW, electric resistance heating section or no heating section | 1: COP = 2.84(3)
[8 empty] | Confinement cell | 7.5 |  |  | Water-cooled air conditioners |  |  |  | 1: ICOP = 2.87
[8 empty] | Copy/Print room | 3.3 |  |  | Direct-expansion ground-source heat pumps |  |  | ≥ 223 kW, non-electric heating section | 1: COP = 2.78(3)
[8 empty] | Corridor/Transition area for hospital | 7.7 |  |  | PTAC |  |  |  | 1: ICOP = 2.81
[8 empty] | Corridor/Transition area for manufacturing facility | 3.1 |  |  | PTHP in cooling mode | ≥ 19 (65 000) | CAN/CSA-C746 | ≥ 19 kW and < 40 kW, electric resistance heating section or no heating section | 1: EER = 11.0
[8 empty] | Corridor/Transition area for space designed to ANSI/IES RP-28 (and used primarily by residents) | 7.7 |  |  | PTHP in heating mode |  |  |  | 1: Heating COP ≥ 3.3 at 8.3°C
[8 empty] | Corridor/Transition area other | 4.4 |  |  | Room air conditioners with reverse cycle |  |  |  | 1: Heating COP ≥ 2.25 at –8.3°C
[8 empty] | Courtroom | 12.9 |  |  | with louvered sides |  |  |  | 1: ICOP = 3.28 (IEER = 11.2)
[8 empty] | Dining area for bar lounge/leisure dining | 9.3 |  |  | without louvered sides |  |  | ≥ 19 kW and < 40 kW, non-electric heating section | 1: EER = 10.8
[8 empty] | Dining area for cafeteria/fast food dining | 4.3 |  |  | Room air conditioners without reverse cycle |  |  |  | 1: Heating COP ≥ 3.3 at 8.3°C
[8 empty] | Dining area for family dining | 6.5 |  |  | Room air conditioners with louvered sides, with reverse cycle |  |  |  | 1: Heating COP ≥ 2.25 at –8.3°C
[8 empty] | Dining area for penitentiary | 4.5 |  |  | Room air conditioners without louvered sides |  |  |  | 1: ICOP = 3.22 (IEER = 11.0)
[8 empty] | Dining area for space designed to ANSI/IES RP-28 (and used primarily by residents) | 13.7 |  |  | Room air conditioner heat pumps with louvered sides |  |  | ≥ 40 kW and < 70 kW, electric resistance heating section or no heating section | 1: EER = 10.6
[8 empty] | Dining area other | 4.7 |  |  | Room air conditioner heat pumps without louvered sides |  |  |  | 1: Heating COP ≥ 3.2 at 8.3°C
[8 empty] | Dressing/Fitting room for performing arts theatre | 4.4 |  |  | Room air conditioner, casement only |  |  |  | 1: Heating COP ≥ 2.05 at –8.3°C
[8 empty] | Electrical/Mechanical room | 4.6 |  |  | Room air conditioner, casement slider |  |  |  | 1: ICOP = 3.14 (IEER = 10.7)
[8 empty] | Emergency vehicle garage | 5.6 |  |  | Air conditioners, air-cooled |  |  | ≥ 40 kW and < 70 kW, non-electric heating section | 1: EER = 10.4
[8 empty] | Food preparation area | 11.7 |  |  | Air conditioners, water-cooled |  |  |  | 1: Heating COP ≥ 3.2 at 8.3°C
[8 empty] | Guest room | 4.4 |  |  | Air conditioners, water-cooled with fluid economizer |  |  |  | 1: Heating COP ≥ 2.05 at –8.3°C
[8 empty] | Laboratory for classroom | 11.9 |  |  | Air conditioners, glycol-cooled |  |  |  | 1: ICOP = 3.08 (IEER = 10.5)
[8 empty] | Laboratory other | 14.3 |  |  | Air conditioners, glycol-cooled with fluid economizer |  |  | ≥ 70 kW, electric resistance heating section or no heating section | 1: EER = 9.5
[8 empty] | Laundry/Washing area | 5.7 |  |  | Chilled water air handler |  |  |  | 1: Heating COP = 3.2 at 8.3°C
[8 empty] | Loading dock – interior | 9.5 |  |  | Vapour compression, air- or water-cooled, electrically operated |  |  |  | 1: Heating COP = 2.05 at –8.3°C
[8 empty] | Lobby for elevator | 7 |  |  | Absorption, single- or double-effect, indirect- |  |  |  | 1: ICOP = 2.81 (IEER = 9.6)
[8 empty] | Lobby for hotel | 5.4 |  |  | or direct-fired |  |  | ≥ 70 kW, non-electric heating section | 1: EER = 9.3
[8 empty] | Lobby for motion picture theatre | 2.5 |  |  | Electric boilers |  |  |  | 1: Heating COP = 3.2 at 8.3°C
[8 empty] | Lobby for performing arts theatre | 13.5 |  |  | Gas-fired boilers |  |  |  | 1: Heating COP = 2.05 at –8.3°C
[8 empty] | Lobby for space designed to ANSI/IES RP-28 (and used primarily by residents) | 18.2 |  |  | Oil-fired boilers (No. 2 oil) |  |  |  | 1: ICOP = 2.75 (IEER = 9.4)
[8 empty] | Lobby other | 9 |  |  | Oil-fired boilers, residual (No. 5 or No. 6 oil) and other oils | — | ANSI/AHRI 390 | < 19 kW | 1: EER = 10(3)
[8 empty] | Locker room | 5.6 |  |  | Gas-fired warm-air furnaces |  | CAN/CSA-C746 | ≥ 19 kW and < 40 kW | 1: EER = 9.5(3)
[8 empty] | Lounge/Break room for health care facility | 4.5 |  |  | Gas-fired duct furnace |  |  | ≥ 40 kW and < 70 kW | 1: EER = 8.6(3)
[8 empty] | Lounge/Break room other | 6.3 |  |  | Gas-fired unit heater | — | ANSI/AHRI 390 | < 19 kW | 1: COP = 3.1(3)
[8 empty] | Office enclosed, ≤ 25 m2 | 8 |  |  | Gas-fired outdoor packaged units |  | CAN/CSA-C746 | ≥ 19 kW and < 40 kW | 1: COP = 3.0(3)
[8 empty] | Office enclosed, > 25 m2 | 7.1 |  |  | Oil-fired warm-air furnace |  |  | ≥ 40 kW and < 70 kW | 1: COP = 2.9(3)
[8 empty] | Office open plan | 6.6 |  |  | Oil-fired duct furnaceand unit heaters | < 19 (65 000) | ANSI/AHRI 210/240 or | < 19 kW | 1: COP = 3.54
[8 empty] | Pharmacy area | 17.9 |  |  |  |  | CTI STD-201OM
[8 empty] | Sales area | 11.3 |  |  |  | ≥ 19 (65 000) and < 70 (240 000) | CAN/CSA-C746 and ANSI/AHRI 340/360 (for IEER) | ≥ 19 kW and < 40 kW, electric resistance heating section or no heating section | 1: COP = 3.37(3)
[8 empty] | Seating area – general | 2.5 | [6 empty] | 1: ICOP = 3.43
[8 empty] | Stairway | The LPD and lighting control requirements for a stairway shall be the same as those for the space containing the stairway. | [6 empty] | 1: (IEER = 11.7)
[8 empty] | Stairwell | 5.3 | [5 empty] | ≥ 19 kW and < 40 kW, non-electric heating section | 1: COP = 3.31(3)
[8 empty] | Parking garage – interior | 1.5 | [6 empty] | 1: ICOP = 3.37
[8 empty] | Storage room < 5 m2 | 5.5 | [6 empty] | 1: (IEER = 11.5)
[8 empty] | Storage room ≥ 5 m2 and ≤ 100 m2 | 4.1 | [5 empty] | ≥ 40 kW and < 70 kW, electric resistance heating section or no heating section | 1: COP = 3.22(3)
[8 empty] | Vehicle maintenance area | 6.5 | [6 empty] | 1: ICOP = 3.28
[8 empty] | Washroom for space designed to ANSI/IES RP-28 (and used primarily by residents) | 13.5 | [6 empty] | 1: (IEER = 11.2)
[8 empty] | Washroom other | 6.8 | [5 empty] | ≥ 40 kW and < 70 kW, non-electric heating section | 1: COP = 3.17(3)
[8 empty] | Workshop | 13.5 | [6 empty] | 1: ICOP = 3.22
[8 empty] | Convention centre – exhibit space | 6.6 | [6 empty] | 1: (IEER = 11.0)
[8 empty] | Dormitory – living quarters | 5.4 |  |  |  | ≥ 70 (240 000) | ANSI/AHRI 340/360 or | ≥ 70 kW, electric resistance heating section or no heating section | 1: COP = 3.22(3)
[8 empty] | Fire station – sleeping quarters | 2.5 |  |  |  |  | CTI STD-201OM |  | 1: ICOP = 3.25
[8 empty] | Gymnasium/Fitness centre exercise area | 9.6 | [6 empty] | 1: (IEER = 11.1)
[8 empty] | Gymnasium/Fitness centre playing area | 9.2 | [5 empty] | ≥ 70 kW, non-electric heating section | 1: COP = 3.17(3)
[8 empty] | Health care facility exam/treatment room | 15.1 | [6 empty] | 1: ICOP = 3.19
[8 empty] | Health care facility imaging room | 10.1 | [6 empty] | 1: (IEER = 10.9)
[8 empty] | Health care facility medical supply room | 6.7 |  |  |  | ≥ 19 (65 000) and < 70 (240 000) | CAN/CSA-C746 | — | 1: EER = 11.2 for air-cooled
[8 empty] | Health care facility nursery | 9.9 | [6 empty] | 1: EER = 13.1 for water-cooled
[8 empty] | Health care facility nurses' station | 12.6 |  |  |  | ≥ 70 (240 000) | ANSI/AHRI 366 (SI) | ≥ 70 kW | 1: COP = 2.96
[8 empty] | Health care facility operating room | 24.3 | [6 empty] | 1: IPLV = 3.28
[8 empty] | Health care facility patient room | 7.3 |  |  |  |  | CTI STD-201OM |  | 1: COP = 3.84
[8 empty] | Health care facility physical therapy room | 9.8 | [6 empty] | 1: IPLV = 3.84
[8 empty] | Health care facility recovery room | 13.5 |  |  |  | < 35 (119 500) | CAN/CSA-C13256-1(4) | — | 1: See standard(3)
[8 empty] | Library reading area | 10.3 |  |  |  | < 40 (136 500) | CAN/CSA-C13256-1 | < 5 kW | 1: Cooling COP = 3.28 at 30°C inlet water and heating COP = 4.2 at 20°C inlet water
[8 empty] | Library stacks | 12.7 | [5 empty] | 5–40 kW | 1: Cooling COP = 3.52 at 30°C inlet water and heating COP = 4.2 at 20°C inlet water
[8 empty] | Manufacturing facility detailed manufacturing area | 8.6 |  |  |  | < 19 (65 000) | ANSI/AHRI 210/240 or CTI STD-201OM | < 19 kW | 1: COP = 3.54(3)
[8 empty] | Manufacturing facility equipment room | 8.2 | [6 empty] | 1: ICOP = 3.60
[8 empty] | Manufacturing facility extra high bay area (> 15 m floor-to-ceiling height) | 15.3 |  |  |  | ≥ 19 (65 000) | ANSI/AHRI 340/360 or CTI STD-201OM | ≥ 19 kW and < 40 kW, electric resistance heating or no heating section | 1: COP = 3.37(3)
[8 empty] | Manufacturing facility high bay area (7.5 m to 15 m floor-to-ceiling height) | 13.4 | [6 empty] | 1: ICOP = 3.43
[8 empty] | Manufacturing facility low bay area (< 7.5 m floor-to-ceiling height) | 9.3 | [5 empty] | ≥ 19 kW and < 40 kW, non-electric heating section | 1: COP = 3.31(3)
[8 empty] | Museum general exhibition area | 3.3 | [6 empty] | 1: ICOP = 3.37
[8 empty] | Museum restoration room | 11.9 | [5 empty] | ≥ 40 kW and < 70 kW, electric resistance heating or no heating section | 1: COP = 3.22(3)
[8 empty] | Post office – sorting area | 8.1 | [6 empty] | 1: ICOP = 3.28
[8 empty] | Religious building fellowship hall | 5.8 | [5 empty] | ≥ 40 kW and < 70 kW, non-electric heating section | 1: COP = 3.17(3)
[8 empty] | Religious building worship/pulpit/choir area | 9.2 | [6 empty] | 1: ICOP = 3.22
[8 empty] | Retail facility dressing/fitting room | 5.4 | [5 empty] | ≥ 70 kW, electric resistance heating or no heating section | 1: COP = 3.22(3)
[8 empty] | Retail facility mall concourse | 8.8 | [6 empty] | 1: ICOP = 3.25
[8 empty] | Space designed to ANSI/IES RP-28 chapel (used primarily by residents) | 7.5 | [5 empty] | ≥ 70 kW, non-electric heating section | 1: COP = 3.17(3)
[8 empty] | Space designed to ANSI/IES RP-28 recreation room (used primarily by residents) | 19 | [6 empty] | 1: ICOP = 3.19
[8 empty] | Sports arena – playing area Class I facility | 31.6 |  |  |  | ≤ 21 (71 700) | CSA C748 | — | 1: See standard
[8 empty] | Sports arena – playing area Class II facility | 21.6 |  |  |  | All capacities | AHRI 310/380/CSA C744 | New construction | 1: COP = 3.66 – (0.213 x Capc/1000)(3)
[8 empty] | Sports arena – playing area Class III facility | 13.9 | [5 empty] | New construction | 1: COP = 3.6 – (0.213 x Capc/1000)(3)
[8 empty] | Sports arena – playing area Class IV facility | 9.3 | [5 empty] | New construction | 1: COP = 3.2 – (0.026 x Capc/1000)(3)
[8 empty] | Transportation facility airport concourse | 2.7 |  |  |  | ≤ 10.55 (36 000) | CSA C368.1 | —
[8 empty] | Transportation facility baggage/carousel area | 4.2 | [6 empty] | 1: EER = 9.0(3)
[8 empty] | Transportation facility terminal ticket counter | 5.5 | [6 empty] | 1: EER = 8.5(3)
[8 empty] | Warehouse – storage area medium to bulky palletized items | 3.6 | [6 empty] | 1: See standard(3)
[8 empty] | Warehouse – storage area small hand-carried items | 7.4 |  |  |  | < 1.8 (6 150) | CSA C368.1 | < 1.8 kW | 1: COP = 2.84(3)
[13 empty] | ≥ 1.8 (6 150) and < 2.3 (7 800) |  | ≥ 1.8 kW and < 2.3 kW | 1: COP = 2.84(3)
[13 empty] | ≥ 2.3 (7 800) and < 4.1 (14 000) |  | ≥ 2.3 kW and < 4.1 kW | 1: COP = 2.87(3)
[13 empty] | ≥ 4.1 (14 000) and < 5.9 (20 150) |  | ≥ 4.1 kW and < 5.9 kW | 1: COP = 2.84(3)
[13 empty] | ≥ 5.9 (20 150) |  | ≥ 5.9 kW | 1: COP = 2.49(3)
[13 empty] | < 2.3 (7 800) |  | < 2.3 kW | 1: COP = 2.64(3)
[13 empty] | ≥ 2.3 (7 800) and < 5.9 (20 150) |  | ≥ 2.3 kW and < 5.9 kW | 1: COP = 2.49
[13 empty] | ≥ 5.9 (20 150) |  | ≥ 5.9 kW | 1: COP = 2.49(3)
[13 empty] | < 5.9 (20 150) |  | < 5.9 kW | 1: COP = 2.65(3)
[13 empty] | ≥ 5.9 (20 150) |  | ≥ 5.9 kW | 1: COP = 2.49(3)
[13 empty] | < 4.1 (14 000) |  | < 4.1 kW | 1: COP = 2.49(3)
[13 empty] | ≥ 4.1 (14 000) |  | ≥ 4.1 kW | 1: COP = 2.34(3)
[13 empty] | All capacities |  | All capacities | 1: COP = 2.55(3)
[13 empty] | All capacities |  | All capacities | 1: COP = 2.78(3)
[13 empty] | < 19 (65 000) | ANSI/ASHRAE 127 | — | 1: SCOP = 2.20 / 2.09
[13 empty] | ≥ 19 (65 000) and < 70 (240 000) |  |  | 1: SCOP = 2.10 / 1.99
[13 empty] | ≥ 70 (240 000) |  |  | 1: SCOP = 1.90 / 1.79
[13 empty] | < 19 (65 000) |  |  | 1: SCOP = 2.60 / 2.49
[13 empty] | ≥ 19 (65 000) and < 70 (240 000) |  |  | 1: SCOP = 2.50 / 2.39
[13 empty] | ≥ 70 (240 000) |  |  | 1: SCOP = 2.40 / 2.29
[13 empty] | < 19 (65 000) |  |  | 1: SCOP = 2.55 / 2.44
[13 empty] | ≥ 19 (65 000) and < 70 (240 000) |  |  | 1: SCOP = 2.45 / 2.34
[13 empty] | ≥ 70 (240 000) |  |  | 1: SCOP = 2.35 / 2.24
[13 empty] | < 19 (65 000) |  | rated at 40% propylene glycol | 1: SCOP = 2.50 / 2.39
[13 empty] | ≥ 19 (65 000) and < 70 (240 000) |  |  | 1: SCOP = 2.15 / 2.04
[13 empty] | ≥ 70 (240 000) |  |  | 1: SCOP = 2.10 / 1.99
[13 empty] | < 19 (65 000) |  |  | 1: SCOP = 2.45 / 2.34
[13 empty] | ≥ 19 (65 000) and < 70 (240 000) |  |  | 1: SCOP = 2.10 / 1.99
[13 empty] | ≥ 70 (240 000) |  |  | 1: SCOP = 2.05 / 1.94
[13 empty] | < 19 (65 000) |  | — | 1: SCOP = 8.00 / 6.06
[13 empty] | ≥ 19 (65 000) and < 70 (240 000) |  |  | 1: SCOP = 9.00 / 7.06
[13 empty] | ≥ 70 (240 000) |  |  | 1: SCOP = 11.00 / 9.06
[13 empty] | < 5 600 (19 000 000) | CAN/CSA-C743 | — | 1: See Tables 9 to 15 in Standard(3)
[13 empty] | — | — | — | bar: 1
[13 empty] | < 88 (300 000) | ANSI Z21.13/CSA 4.9 | — | 1: AFUE = 85%(3)
[13 empty] | ≥ 88 (300 000) and < 733 (2 500 000) | ANSI Z21.13/CSA 4.9 or ASME PTC 4 | — | 1: Et ≥ 83.0%
[13 empty] | ≥ 733 (2 500 000) |  | — | 1: Ec ≥ 83.3%
[13 empty] | < 88 (300 000) | CSA P.2 or ASME PTC 4 | — | 1: AFUE ≥ 84.7%(3)
[13 empty] | ≥ 88 (300 000) and < 733 (2 500 000) |  |  | 1: Et ≥ 83.4%
[13 empty] | ≥ 733 (2 500 000) |  |  | 1: Ec ≥ 85.8%
[13 empty] | < 88 (300 000) | CSA P.2 | — | 1: AFUE ≥ 84.7%(3)
[13 empty] | ≥ 88 (300 000) and < 733 (2 500 000) | ASME PTC 4 |  | 1: Et ≥ 83.4%
[13 empty] | ≥ 733 (2 500 000) |  |  | 1: Ec ≥ 85.8%
[13 empty] | ≤ 66 (225 000) | CSA P.2 | — | 1: AFUE ≥ 92.4%(3)
[13 empty] | > 66 (225 000) | CAN/CSA-P.8 | Maximum rated capacity, steady-state | 1: Et ≥ 81%
[13 empty] | ≤ 117.23 (400 000) | ANSI Z83.8/CSA 2.6 | — | 1: Et ≥ 81%
Et ≥ 82%(3)
[13 empty] | > 65.9 kW (225 000) and < 2 930 kW (10 000 000) | CAN/CSA-P.8(8) |  | 1: Et ≥ 80%
[13 empty] | ≤ 66 (225 000) | CSA P.2 |  | 1: Et ≥ 84.5%(3)
SEUE ≥ 78%
[13 empty] | > 66 (225 000) | CAN/CSA-B140.4 |  | 1: Et ≥ 81.3%
[13 empty] | — |  |  | 1: Et ≥ 81%
Table 5.2.12.2.
Cooling tower - centrifugal fan, direct-contact
Cooling tower - propeller or axial fan, direct-contact
Cooling tower - centrifugal fan, indirect-contact evaporative
Cooling tower - propeller or axial fan, indirect-contact evaporative
Condenser - centrifugal, indirect-contact evaporative
Condenser - propeller or axial fan, indirect-contact evaporative
Condenser - air cooled

## Energy Checklist - Alterations
Energy Checklist for Alterations to Existing NECB/ZEBP Buildings
[5 empty] | (See NECB/ZEBP alteration requirements) | [21 empty] | Building Use description will appear here.
Building Address : | [5 empty] | 37 |  |  | 2203 |  |  | ABERDEEN STREET | [5 empty] | Building Permit Application No.:
Tenancy Address :
This form is to be completed digitally. For ease of use, drop boxes and pop-up instructions are included.
IMPORTANT - Submission Format and Process:
Effective June 3, 2019, this Alterations checklist is to be completed and submitted at the Building Permit application stage. Submit online with your Building Permit application. Include all relevent documents pertaining to scope of work.
Space Use, Area & Performance Information
| Primary Use/Area: | [14 empty] | TI Space(s) | Non-residential Cond'd Space Area (m2):
| Second Use/Area: | [15 empty] | Resid Cond'd Common Space Area (m2):
| Tertiary Use/Area: | [15 empty] | Semiheated Space Area (m2):
| Total Area (m2): |  |  |  |  | Building Use Description | [10 empty] | Is public access via an outdoor entrance?
Is existing outdoor entrance being modified?
Neighbourhood Energy (N/E) Systems
| Rz Cond's |  | EUI required: | [5 empty] | Energy reduction: | [5 empty] | LEED ver: |  |  | LEED targets:
|  |  | achieved: | [6 empty] | achieved: | [8 empty] | achieved:
Renewable / High Performance Energy Systems
- Renewable Energy systems:
- High Performance Energy systems:
If within a Neighbourhood Energy area, indicate which system:
| Base Building's N/E status: | [17 empty] | TI's thermal energy requirement: | N/A
| VBBL (11.7.1.1.(3)(b)) - Alterations per NECB/ZEBP Deliverables | [21 empty] | Are Reg'd Professionals involved with this project?
10.2.2.22 - Does the proposed scope of work include the design and provision of exterior patio/space heating systems?
| NECB Part 3) Building Envelope | [7 empty] | Info | [13 empty] | Applicability:
|  |  |  | Building Envelope Compliance Table (tab below) | [10 empty] | N/A |  | Energy Statements on Drawings | [5 empty] | Dwg #: | N/A
| or; |  |  | Building Envelope Energy Perf Comparison Calc | [12 empty] | Complies with NECB Envelope Alterations (2.1.1)
| NECB Part 4) Lighting | [7 empty] | Info | [13 empty] | Applicability:
|  |  |  | Lighting Alteration Compliance Table (tab below) | [10 empty] | N/A |  | Energy Statements on Drawings | [5 empty] | Dwg #: | N/A
|  |  |  | Complies with NECB Lighting Alterations (2.1.2.) | [12 empty] | Drawing: Reflected Ceiling Plan | [5 empty] | Dwg #:
| NECB Part 5) HVAC | [7 empty] | Info | [13 empty] | Applicability:
|  |  |  | HVAC Alteration Compliance Table (tab below) | [10 empty] | N/A |  | Energy Statements on Drawings | [5 empty] | Dwg #: | N/A
|  | Source of Ventilation design: | [14 empty] | Complies with NECB HVAC Additions (2.1.3.1.)
Complies with NECB HVAC Alterations (2.1.3.2.)
| NECB Part 6) Service Water Htg | [7 empty] | Info | [13 empty] | Applicability:
|  |  |  | Service Water Htg Compliance Table (tab below) | [10 empty] | N/A |  | Energy Statements on Drawings | [5 empty] | Dwg #: | N/A
|  |  |  | Electric/Gas Water Heating System is Allowed | [12 empty] | Complies with NECB SWH Alterations (2.1.4.)
| NECB Part 7) Power | [7 empty] | Info | [13 empty] | Applicability:
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [16 empty] | DOC/2012/155502 |  |  |  | Version: |  | 230707-1
Drop Down Boxes
| Box 1 |  |  | Box 2 |  |  | Renewable Energy | [5 empty] | Box 4 |  | Construction Types |  |  |  | Box 6 |  | N/E | [6 empty] | Box 8
| Yes |  |  | Yes |  |  | N/A | [5 empty] | X |  | Voluntary Upgrade |  |  |  | Yes |  | Use Base Building N/E System | [6 empty] | X
| No |  |  | No |  |  | Photovoltaic systems | [5 empty] | N/A |  | Repair |  |  |  | N/A |  | None
|  |  |  | N/A |  |  | Solar Thermal systems | [7 empty] | Small Suite | [5 empty] | N/A
[7 empty] | Bio-fuel based energy | [7 empty] | Minor Reno
[7 empty] | Geothermal Heating | [7 empty] | Change MOC
[7 empty] | Geothermal Electric | [7 empty] | Major Reno
[7 empty] | Low-impact Hydro Electric | [7 empty] | Alteration (Add'n)
[7 empty] | Wave & Tidal Power | [7 empty] | Relocation
| LEED Version | [6 empty] | LEED Certif | [6 empty] | Building Use(s) |  |  |  | Building Use(s)
| N/A | [17 empty] | Building Use Description | [5 empty] | Building Use description will appear here.
| LEED v1.0 | [6 empty] | N/A | [6 empty] | Unknown (Core & Shell) |  |  |  | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
| LEED v1.1 | [6 empty] | Platinum | [6 empty] | Bank Branch |  |  |  | Bank Branch | [5 empty] | Bank Branch refers to a commercial banking outlet that offers banking services to walk-in customers. Gross Floor Area should include all space within the building(s), including banking areas, vaults, lobbies, atriums, kitchens used by staff, conference rooms, storage areas, stairways, and elevator shafts.
| LEED 2009 | [6 empty] | Gold | [6 empty] | Data Centre |  |  |  | Data Centre | [5 empty] | Data Center refers to buildings specifically designed and equipped to meet the needs of high density computing equipment, such as server racks, used for data storage and processing. Typically these facilities require dedicated uninterruptible power supplies and cooling systems. Data center functions may include traditional enterprise services, on-demand enterprise services, high performance computing, internet facilities, and/or hosting facilities. Often Data Centers are free standing, mission critical computing centers. When a data center is located within a larger building, it will usually have its own power and cooling systems, and require a constant power load of 75 kW or more. Data Center is intended for sophisticated computing and server functions; it should not be used to represent a server closet or computer training area. Gross Floor Area should include all space within the building(s) including raised floor computing space, server rack aisles, storage silos, control console areas, battery rooms, mechanical rooms for cooling equipment, administrative office areas, elevator shafts, stairways, break rooms and restrooms.
| LEED Mid Rise | [6 empty] | Silver | [6 empty] | Distribution Centre |  |  |  | Distribution Centre | [5 empty] | Distribution Center refers to unrefrigerated buildings that are used for the temporary storage and redistribution of goods, manufactured products, merchandise or raw materials. Gross Floor Area should include all space within the building(s) including space designed to store non-perishable goods and merchandise, offices, lobbies, stairways, rest rooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
| LEED v4 | [6 empty] | Certified | [6 empty] | Education (Adult C Educ) |  |  |  | Education (Adult C Educ) | [5 empty] | Adult Education refers to buildings used primarily for providing adult students with continuing education, workforce development, or professional development outside of the college or university setting. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, auditoriums, stairways, atriums, elevator shafts, and storage areas.
[15 empty] | Education (College/Univ) |  |  |  | Education (College/Univ) | [5 empty] | College/University refers to buildings used for the purpose of higher education. This includes public and private colleges and universities. Gross Floor Area should include all space within the building(s), including classrooms, laboratories, offices, cafeterias, maintenance facilities, arts facilities, athletic facilities, residential areas, storage rooms, restrooms, elevator shafts, and stairways.
[15 empty] | Education (K-12) |  |  |  | Education (K-12) | [5 empty] | K-12 School refers to buildings or campuses used as a school for Kindergarten through 12th grade students. This does not include college or university classroom facilities/laboratories, or vocational, technical, trade, adult, or continuing education schools. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, laboratory classrooms, portable classrooms, greenhouses, stairways, atriums, elevator shafts, small landscaping sheds, and storage areas. The ENERGY STAR score for K-12 School does not apply to preschool or day care buildings; in order to classify as K-12 school, more than 75% of the students must be in kindergarten or older.
| LEED Type | [13 empty] | Education (Pre/Daycare) |  |  |  | Education (Pre/Daycare) | [5 empty] | Pre-school/Daycare applies to buildings used for educational programs or daytime supervision/recreation for young children before they attend Kindergarten. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, stairways, elevator shafts, and storage areas.
[15 empty] | Education (Vocational) |  |  |  | Education (Vocational) | [5 empty] | Vocational School refers to buildings primarily designed to teach skilled trades to students, including trade and technical schools. Typically vocational schools are commonly post-secondary education, consisting of 1-2 years of technical/trade training. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, laboratory classrooms, stairways, elevator shafts, and storage areas.
| N/A | [13 empty] | Food (Fast Food Rest) |  |  |  | Food (Fast Food Rest) | [5 empty] | Fast Food Restaurant, also known as Quick Service Restaurant, refers to buildings used for the preparation and sale of ready-to-eat food. Fast Food Restaurants are characterized by a limited menu of food prepared quickly (often within a few minutes), and sometimes cooked in bulk in advance and kept hot. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, offices, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
| LEED NC - New Const'n | [13 empty] | Food (Restaurant) |  |  |  | Food (Restaurant) | [5 empty] | Restaurant refers to buildings used for preparation and sale of ready-to-eat food and beverages, but which do not fit in the fast food property type. Examples include fast casual, casual, and fine dining restaurants. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, offices, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
| LEED CS - Core & Shell | [13 empty] | Food Sales (specialty) |  |  |  | Food Sales (specialty) | [5 empty] | Food Sales refers to buildings used for the sales of food on either a retail or wholesale basis, but which do not meet the definition of Supermarket/Grocery Store, Convenience Store, or Convenience Store with Gas Stations. For example, specialty food sales like a cheese shop or butcher. Gross Floor Area should include all space within the building(s), including sales areas, storage areas, offices, kitchens, and staff break rooms.
[15 empty] | Food Service |  |  |  | Food Service | [5 empty] | Food Service refers to buildings used for preparation and sale of food and beverages, but which do not meet the definition of Restaurant, Cafeteria, or Bar/Nightclub. For example a bakery or coffee shop. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
[15 empty] | Gov (Convention Ctr) |  |  |  | Gov (Convention Ctr) | [5 empty] | Convention center refers to buildings used primarily for large conferences, exhibitions, and similar events. Convention centers may include a diverse variety of spaces, including large exhibition halls, meeting rooms, and concession stands. Gross Floor Area should include all space within the building(s), including exhibit halls, preparation and staging areas, meeting rooms, concession stands, offices, bathrooms, break rooms, security areas, elevator shafts, and stairwells. Loading dock areas located outside the walls of the building should not be included in the gross square footage.
| High Performance Energy | [13 empty] | Gov (Courthouse) |  |  |  | Gov (Courthouse) | [5 empty] | Courthouse refers to buildings used for federal, state, or local courts, and associated administrative office space. Gross Floor Area should include all space within the building(s), including temporary holding cells, chambers, kitchens used by staff, lobbies, atriums, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
[15 empty] | Gov (Fire Station) |  |  |  | Gov (Fire Station) | [5 empty] | Fire Station refers to buildings used to provide emergency response services associated with fires. Fire stations may be staffed by either volunteer or full-time paid firemen. Gross Floor Area should include all space within the building(s), including office areas, vehicle storage areas, residential areas (if applicable), storage areas, break rooms, kitchens, elevator shafts, and stairwells.
| N/A | [13 empty] | Gov (Library) |  |  |  | Gov (Library) | [5 empty] | Library refers to buildings used to store and manage collections of literary and artistic materials such as books, periodicals, newspapers, films, etc. that can be used for reference or lending. Gross Floor Area should include all space within the building(s), including circulation rooms, storage areas, reading/study rooms, administrative space, kitchens used by staff, lobbies, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Ground Source Heat Pump | [13 empty] | Gov (Police Station) |  |  |  | Gov (Police Station) | [5 empty] | Police Station applies to buildings used for federal, state, or local police forces and their associated office space. Gross Floor Area should include all space within the building(s), including offices, temporary holding cells, kitchens used by staff, lobbies, atriums, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Air Source Heat Pump | [13 empty] | Gov (Post Office) |  |  |  | Gov (Post Office) | [5 empty] | Mailing Center/Post Office refers to buildings used as retail establishments dedicated to mail and mailing supplies. This includes U.S. Post Offices, in addition to private retailers that offer priority mail services and mailing supplies. Gross Floor Area should include all space within the building(s), including retail counters, administrative space, kitchens used by staff, lobbies, conference rooms, storage areas, stairways, and mechanical rooms.
| Waste Heat Recovery (All types) | [13 empty] | Gov (Prison) |  |  |  | Gov (Prison) | [5 empty] | Prison/Incarceration refers to federal, state, local, or private-sector buildings used for the detention of persons awaiting trial or convicted of crimes. Gross Floor Area should include all space within the building(s), including holding cells, cafeterias, administrative spaces, kitchens, lobbies, atriums, conference rooms and auditoriums, fitness areas, storage areas, stairways, and elevator shafts.
[15 empty] | Hotel |  |  |  | Hotel | [5 empty] | Hotel refers to buildings renting overnight accommodations on a room/suite and nightly basis, and typically include a bath/shower and other facilities in guest rooms. Hotel properties typically have daily services available to guests including housekeeping/laundry and a front desk/concierge. Hotel does not apply to properties where more than 50% of the floor area is occupied by fractional ownership units such as condominiums or vacation timeshares, or to private residences that are rented out on a daily or weekly basis. Hotel properties should be majority-owned by a single entity and have rooms available on a nightly basis. Condominiums or Time Shares should select the Multifamily Housing property use. Gross Floor Area should include all interior space within the building(s), including guestrooms, halls, lobbies, atriums food preparation and restaurant space, conference and banquet space, fitness centers/spas, indoor pool areas, laundry facilities, elevator shafts, stairways, mechanical rooms, storage areas, employee break rooms, and back-of-house offices.
[15 empty] | Laboratory |  |  |  | Laboratory | [5 empty] | Laboratory refers to buildings that provide controlled conditions in which scientific research, measurement, and experiments are performed or practical science is taught. Gross Floor Area should include all space within the building(s) including workstations/hoods, offices, conference rooms, storage areas, decontamination rooms, mechanical rooms, elevator shafts, and stairwells.
[15 empty] | Manuf/Indust Plant |  |  |  | Manuf/Indust Plant | [5 empty] | Manufacturing/Industrial Plant refers to buildings used for manufacturing or assembling goods. Typically a Manufacturing/Industrial plant includes a main production area that has high-ceilings and contains heavy equipment used for assembly line production. Gross Floor Area should include all space within the building(s) at the plant, including production areas, offices, conference rooms, employee break rooms, storage areas, mechanical rooms, stairways, and elevator shafts.
[15 empty] | Medical (Amb Surg Ctr) |  |  |  | Medical (Amb Surg Ctr) | [5 empty] | Ambulatory Surgery Centers refers to health care facilities that provide same-day surgical care, including diagnostic and preventive procedures. Gross Floor Area should include all space within the building(s) including offices, operating and recovery rooms, waiting rooms, employee break rooms and kitchens, elevator shafts, stairways, mechanical rooms, and storage areas.
| Applicability | [13 empty] | Medical (Clinic/Emerg) |  |  |  | Medical (Clinic/Emerg) | [5 empty] | Urgent Care Center/Clinic/Other Outpatient Office refers to buildings used to treat patients, usually on an unscheduled, walk-in basis, who have an injury or illness that requires immediate care but is not serious enough to warrant a visit to an emergency department. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
[15 empty] | Medical (Hospital) |  |  |  | Medical (Hospital) | [5 empty] | Hospital refers to a general medical and surgical hospital (including critical access hospitals and children’s hospitals). These facilities provide acute care services intended to treat patients for short periods of time, including emergency medical care, physician's office services, diagnostic care, ambulatory care, surgical care, and limited specialty services such as rehabilitation and cancer care. The definition of Hospital accounts for all space types owned by the hospital that are located within the Hospital building/campus, including non-clinical spaces such as administrative offices, food service, retail, hotels, and power plant. Gross Floor Area should include all space within the building(s) on the campus including operating rooms, bedrooms, emergency treatment areas, medical offices, exam rooms, laboratories, lobbies, atriums, cafeterias, rest rooms, stairways, corridors connecting buildings, storage areas, and elevator shafts. More than 50% of the gross floor area of all buildings must be used for general medical and surgical services and more than 50% of the licensed beds must provide acute care services. Properties that use more than 50% of the gross floor area for long-term care (including long-term acute care), skilled nursing, specialty care, and/or ambulatory surgical centers or that have less than 50% of their beds licensed for acute care services are not eligible for an ENERGY STAR score. If your facility does not meet this definition, it is not eligible for an ENERGY STAR score as Hospital. You can choose from the other available healthcare property types: Ambulatory Surgical Center, Medical Office, Other/Specialty Hospital, Outpatient Rehabilitation/Physical Therapy, Urgent Care/Clinic/Other Outpatient, or Senior Care Community.
| Yes |  | Applies | [11 empty] | Medical (PT/Rehab) |  |  |  | Medical (PT/Rehab) | [5 empty] | Outpatient Rehabilitation/Physical Therapy offices refers to buildings used to provide diagnosis and treatment for rehabilitation and physical therapy. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, indoor pool areas, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
| No |  | N/A | [11 empty] | Medical (Vet Office) |  |  |  | Medical (Vet Office) | [5 empty] | A Veterinary Office refers to buildings used for the medical care and treatment of animals. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
[15 empty] | Medical Office |  |  |  | Medical Office | [5 empty] | Medical Office refers to buildings used to provide diagnosis and treatment for medical, dental, or psychiatric outpatient care. Gross Floor Area should include all space within the building(s) including offices, exam rooms, laboratories, lobbies, atriums, conference rooms and auditoriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
| Base Building's N/E status | [13 empty] | Office |  |  |  | Office | [5 empty] | Office refers to buildings used for the conduct of commercial or governmental business activities. This includes administrative and professional offices. Gross Floor Area should include all space within the building(s) including offices, conference rooms and auditoriums, kitchens used by staff, lobbies, fitness areas for staff, storage areas, stairways, and elevator shafts.
[15 empty] | Office (Financial) |  |  |  | Office (Financial) | [5 empty] | Financial Office refers to buildings used for financial services such as bank headquarters and securities and brokerage firms. Gross Floor Area should include all space within the building(s) including offices, trading floors, conference rooms and auditoriums, vaults, kitchens used by staff, lobbies, atriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Connected to N/E System | [13 empty] | Other |  |  |  | Other | [5 empty] | "Other" refers to buildings that do not fall within the available property use categories in Portfolio Manager. Before selecting Other, it is highly recommended that you review the full list of property uses available for selection to ensure that there is not a suitable category for your property. Gross Floor Area should include all space within the building(s), including space devoted to your main business activity, administrative offices, employee break rooms, bathrooms, stairways, and elevator shafts.
| Not Connected to N/E System | [13 empty] | Other (Education) |  |  |  | Other (Education) | [5 empty] | Other – Education refers to buildings used for religious, community, or other educational purposes not described in the available property uses in Portfolio Manager (i.e educational purposes other than adult education, college/university, K-12 school, pre-school/daycare and vocational schools). Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, auditoriums, laboratory classrooms, stairways, elevator shafts, and storage areas.
| N/A | [13 empty] | Other (Entertainment) |  |  |  | Other (Entertainment) | [5 empty] | Other - Entertainment/Public Assembly refers to buildings whose primary use is for entertainment or public gatherings and that do not meet the definition of any other property use defined in Portfolio Manager. Gross floor area should include all space within the building(s), including entertainment areas, administrative areas, and supporting areas such as storage rooms, hallways, restrooms, stairways, and maintenance areas.
[15 empty] | Other (Lodging/Res) |  |  |  | Other (Lodging/Res) | [5 empty] | Other – Lodging/Residential refers to buildings used for residential purposes other than multifamily residential, single family home, senior care community, residence hall/dormitory, barracks, prison/incarceration, or hotel. Gross Floor Area should include all space within the building(s), including living areas, common areas, administrative space, kitchens used by staff, lobbies, waiting areas, cafeterias, stairways, atriums, elevator shafts, and storage areas.
[15 empty] | Other (Mall) |  |  |  | Other (Mall) | [5 empty] | Other - Mall refers to buildings containing a collection of stores whose purpose is the sale of goods, but which do not fit into the enclosed mall, lifestyle center, or strip mall property types. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, storage areas, staff break rooms, walkways, stairwells, and mechanical areas.
[15 empty] | Other (Public Services) |  |  |  | Other (Public Services) | [5 empty] | Other – Public Services refers to buildings used by public-sector organizations to provide public services other than those described in the available property uses in Portfolio Manager (i.e. services other than offices, courthouses, drinking water treatment and distribution plants, fire stations, libraries, mailing centers or post offices, police stations, prisons or incarceration facilities, social or meeting halls, transportation terminals or stations, or wastewater treatment plants). Gross Floor Area should include all space within the building(s), including administrative space, kitchens used by staff, lobbies, waiting areas, cafeterias, stairways, atriums, elevator shafts, landscaping sheds, and storage areas.
| Neighbourhood Energy Systems | [13 empty] | Other (Recreation) |  |  |  | Other (Recreation) | [5 empty] | Other - Recreation refers to buildings primarily used for recreation that do not meet the definition of any other property use defined in Portfolio Manager. Gross Floor Area should include all space within the building(s), including recreational areas and supporting activities such as mechanical rooms, storage areas, elevator shafts, and stairwells.
[15 empty] | Other (Rest/Bar) |  |  |  | Other (Rest/Bar) | [5 empty] | Other – Restaurant/Bar refers to buildings used for preparation and sale of ready-to-eat food and beverages, but which does not fit into the fast food restaurant, restaurant, or bar/nightclub property types. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
[15 empty] | Other (Services) |  |  |  | Other (Services) | [5 empty] | Other - Services refers to buildings in which primarily services are offered, but which does not fit into the Personal Services or Repair Services property types. Examples include kennels, photo processing shops, etc. Gross Floor Area should include all space within the building(s), including sales floors, offices, storage areas, staff break rooms, walkways, and stairwells.
| Choose One | [13 empty] | Other (Specialty Hosp) |  |  |  | Other (Specialty Hosp) | [5 empty] | Other/Specialty Hospitals refers to long-term acute care hospitals, inpatient rehabilitation facilities, including Cancer Centers and Psychiatric and Substance Abuse Hospitals/Facilities. Gross Floor Area should include all space within the building(s) on the campus including: medical offices, patient rooms, laboratories, lobbies, atriums, cafeterias, rest rooms, stairways, corridors connecting buildings, storage areas, elevator shafts.
| N/A | [13 empty] | Other (Stadium) |  |  |  | Other (Stadium) | [5 empty] | Other - Stadium refers to buildings primarily used for sporting events that do not meet the definition of any other property use defined in Portfolio Manager. Gross Floor Area should include all space within the building(s), including areas for athletic activity and spectator seating and supporting activities such as mechanical rooms, storage areas, elevator shafts, and stairwells.
| Creative Energy (Central Heat) N/E system | [13 empty] | Other (Tech) |  |  |  | Other (Tech) | [5 empty] | Other – Technology/Science refers to buildings used for science and technology related services other than Laboratories and Data Centers. Gross Floor Area should include all space within the building(s), including areas with the main business activity, production areas, administrative offices, employee break areas, stairways, atriums, elevator shafts, and storage areas.
| City Owned False Creek NEU Service Area | [13 empty] | Other (Utility) |  |  |  | Other (Utility) | [5 empty] | Other – Utility applies to buildings used by a utility for some purpose other than general office or energy/power generation. This may include utility transfer stations or maintenance facilities. Note that an administrative office occupied by a utility should be entered as Office, and a power or energy generation plant should be entered as Energy/Power Station. Gross Floor Area should include all space within the building(s), including administrative space, maintenance and equipment areas, generator rooms, kitchens used by staff, lobbies, meeting rooms, stairways, elevator shafts, and storage areas. This should not include any exterior spaces associated with utility operations.
| East Fraserlands (River District) N/E system | [13 empty] | Parking |  |  |  | Parking | [5 empty] | Parking refers to buildings and lots used for parking vehicles. This includes open parking lots, parking structures that may be only partially enclosed, and fully-enclosed (or underground) parking structures. Parking structures may be free standing or may be physically connected to another building.
| Total site of 8,000 m2 or greater | [13 empty] | Personal Services |  |  |  | Personal Services | [5 empty] | Personal Services refers to buildings used to sell services rather than physical goods. Examples include dry cleaners, salons, spas, etc. Gross Floor Area should include all space within the building(s), including sales floors, offices, storage areas, staff break rooms, walkways, and stairwells.
| Total new development of 45,000 m2 or greater | [13 empty] | Rec (Aquarium) |  |  |  | Rec (Aquarium) | [5 empty] | Aquarium refers to buildings used to provide aquatic habitat primarily to live animals and which may include public or private viewing areas and educational programs. Gross Floor area should include public and restricted areas such as visitor walkways, tank space, retail areas, restaurants, laboratories, classrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Areas not in enclosed buildings, such as outdoor habitats, open-air theaters, walkways, and landscaped areas should not be included in the Gross Floor Area.
[15 empty] | Rec (Arena - indoor) |  |  |  | Rec (Arena - indoor) | [5 empty] | Indoor Arena refers to enclosed structures used for professional or collegiate sports and entertainment events. Examples of events held in indoor arenas include basketball and hockey games, circus performances, and concerts. Indoor Arenas usually have capacities of 5,000 seats or more and are often characterized by multiple concourses and concession areas.
[15 empty] | Rec (Bar/Nightclub) |  |  |  | Rec (Bar/Nightclub) | [5 empty] | Bar/Nightclub refers to buildings used primarily for social/entertainment purposes, and is characterized by most of the revenue being generated from the sale of beverages instead of food. Gross Floor Area should include all space within the building(s), including standing/seating areas, stage/dressing room areas, food/drink preparation or kitchen areas, retail areas, bathrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Properties whose primary business revenues are generated from the sale of food should be entered using one of the Restaurant property uses, even if there is a bar.
[15 empty] | Rec (Bowling Alley) |  |  |  | Rec (Bowling Alley) | [5 empty] | Bowling alley refers to buildings used for public or private, recreational or professional bowling. Gross Floor Area should include all space within the building(s), including bowling lanes, concession areas, party rooms, retail areas, administrative/office space, employee break rooms, storage areas, and mechanical rooms.
[15 empty] | Rec (Casino) |  |  |  | Rec (Casino) | [5 empty] | Casino refers to buildings primarily used to conduct gambling activities including both electronic and live table games. Gross Floor Area should include all space within the building(s), including the main casino floor/gaming area, restaurants/bars, retail areas, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. If your Casino is located in the same building as a hotel, we recommend that you enter a separate hotel property use.
[15 empty] | Rec (Fitness Ctr/Gym) |  |  |  | Rec (Fitness Ctr/Gym) | [5 empty] | Fitness Center/Health Club/Gym refers to buildings used for recreational or professional athletic training and related activities. Gross Floor Area should include all space within the building(s), including weight and cardio equipment areas, personal training areas, courts, locker rooms, sauna and spa areas, retail areas, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
[15 empty] | Rec (Ice/Curling Rink) |  |  |  | Rec (Ice/Curling Rink) | [5 empty] | Ice/Curling Rink refers to buildings that include one or more ice sheets used for public or private, recreational or professional skating, curling, hockey, or other similar activities. Gross Floor Area should include all space within the building(s), including ice area, spectator areas, concession stands, retail areas, locker rooms, administrative/office areas, employee break rooms, mechanical rooms, and storage areas. Larger facilities primarily serving professional or collegiate functions and with significant spectator seating should review the definition for Indoor Arena to determine the best classification.
| Renewable & HP Energies | [13 empty] | Rec (Movie Theatre) |  |  |  | Rec (Movie Theatre) | [5 empty] | Movie theater refers to buildings used for public or private film screenings. Gross Floor Area should include all space within the building(s), including seating areas, lobbies, concession stands, bathrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
[15 empty] | Rec (Museum) |  |  |  | Rec (Museum) | [5 empty] | Museum refers to buildings that display collections to outside visitors for public viewing and enjoyment and for informational/educational purposes. Gross Floor Area should include all space within the building(s), including public collection display areas, meeting rooms, classrooms, gift shops, food service areas, administrative/office space, mechanical rooms, storage areas for collections, elevator shafts, and stairwells.
| Photovoltaic systems | [13 empty] | Rec (Performing Arts) |  |  |  | Rec (Performing Arts) | [5 empty] | Performing Arts refers to buildings used for public or private artistic or musical performances. Gross Floor Area should include all space within the building(s), including seating, stage and backstage areas, food service areas, retail areas, rehearsal studios, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
| Solar Thermal systems | [13 empty] | Rec (Race Track) |  |  |  | Rec (Race Track) | [5 empty] | Race Track refers to buildings used primarily to hold racing events such as vehicle races, track/field races, horse races, and/or dog-races. Gross Floor Area should include all spectator viewing areas, concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the race track itself should also be included in the gross floor area, along with the footprint of any staging areas.
| Bio-fuel based energy | [13 empty] | Rec (Roller Rink) |  |  |  | Rec (Roller Rink) | [5 empty] | Roller Rink refers to buildings used primarily for roller-skating, inline skating/rollerblading, or skateboarding. Gross Floor Area should include all space within the building(s), including the rink space, concession areas, locker rooms, retail areas, administrative/office areas, employee break rooms, mechanical rooms, and storage areas.
| Geothermal Heating | [13 empty] | Rec (Social/Mtg Hall) |  |  |  | Rec (Social/Mtg Hall) | [5 empty] | Social/Meeting hall refers to buildings primarily used for public or private gatherings. This may include community group meetings, seminars, workshops, or performances. Please note that there is another property use available, Convention Center, for large exhibition and conference facilities. Gross Floor Area should include all space within the building(s), including meeting rooms, auditoriums, food service areas, lobbies, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
| Geothermal Electric | [13 empty] | Rec (Stadium - closed) |  |  |  | Rec (Stadium - closed) | [5 empty] | Stadium (Closed) refers to structures with a permanent or retractable roof which are used primarily for professional or collegiate sports and entertainment events. Examples of events held in closed stadiums include baseball and football games, and concerts. Closed Stadiums usually have capacities of 25,000 seats or more and are often characterized by multiple concourses and concession areas. Gross Floor Area should include all space within the building(s), including concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the playing field should also be included in the gross floor area.
| Ground Source Heat Pump | [13 empty] | Rec (Stadium - open) |  |  |  | Rec (Stadium - open) | [5 empty] | Stadium (Open) refers to structures used primarily for professional or collegiate sports and entertainment events in which the playing field is not covered and is exposed to the outside. Examples of events held in open stadiums include baseball, football, and soccer games, and concerts. Open Stadiums usually have capacities of 5,000 seats or more and are often characterized by multiple concourses and concession areas. Gross Floor Area should include all space within the building(s), including concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the playing field should also be included in the gross floor area.
| Air Source Heat Pump | [13 empty] | Rec (Swimming Pool) |  |  |  | Rec (Swimming Pool) | [5 empty] | Swimming Pool refers to any heated swimming pools located either inside or outside. To enter a swimming pool, a specific pool size must be selected. In order to enter buildings associated with a Swimming Pool, the main property use must be entered (e.g., K-12 School, Hotel, Fitness Center/Health Club/Gym, etc).
| Waste Heat Recovery (All types) | [13 empty] | Rec (Zoo) |  |  |  | Rec (Zoo) | [5 empty] | Zoo refers to buildings used primarily to provide habitat to live animals and which may include public or private viewing and educational programs. Gross Floor Area should include all space within all fully enclosed buildings, including, habitats, visitor viewing areas, theaters, classrooms, food service areas, retail stores, veterinary offices, exhibit space, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Areas not in fully enclosed buildings, such as outdoor habitats, open-air theaters, walkways, and landscaped areas should not be included in the Gross Floor Area.
[15 empty] | Residential (Barracks) |  |  |  | Residential (Barracks) | [5 empty] | Barracks refers to residential buildings associated with military facilities or educational institutions which offer multiple accommodations for long-term residents. Gross Floor Area should include all space within the building(s), including bedrooms, common areas, food service facilities, laundry facilities, meeting spaces, exercise rooms, health club/spas, lobbies, elevator shafts, storage areas, and stairways.
[15 empty] | Residential (Hall/Dorm) |  |  |  | Residential (Hall/Dorm) | [5 empty] | Residence Hall/Dormitory refers to buildings associated with educational institutions or military facilities which offer multiple accommodations for long-term residents. Gross Floor Area should include all space within the building(s), including bedrooms, common areas, food service facilities, laundry facilities, meeting spaces, exercise rooms, health club/spas, lobbies, elevator shafts, storage areas, and stairways.
[15 empty] | Res (Multifamily-Common Areas) |  |  |  | Res (Multifamily-Common Areas) | [5 empty] | Multifamily-Common Areas refers only to the common areas of residential buildings that contain more than two residential living units. These properties may be high rise buildings (4 or more stories), or mixed use buildings of 3 stories or less. Occupants of these buildings may include tenants, cooperators, and/or individual owners. IMPORTANT: Work done on the building's envelope is considered base building work and should use this checklist. For work done within residential suites, applicants are to use the Alterations to Residential Suites checklist.
[15 empty] | Residential (Senior Care) |  |  |  | Residential (Senior Care) | [5 empty] | Senior Care Community refers to buildings that house and provide care and assistance for elderly residents. Gross Floor Area should include all space within the building(s) including individual rooms or units, wellness centers, exam rooms, community rooms, small shops or service areas for residents and visitors (e.g. hair salons, convenience stores), staff offices, lobbies, atriums, cafeterias, kitchens, storage areas, hallways, basements, stairways, corridors between buildings, and elevator shafts. The ENERGY STAR score for Senior Care community applies to nursing homes (skilled nursing facilities) and assisted living facilities. Independent senior living communities are not eligible. However, it is common for some Senior Care Communities to offer a mix of residential options including independent living, assisted living, and skilled nursing. More than 50% of the units in a community must be considered skilled nursing and/or assisted living in order to be eligible for an ENERGY STAR score as a Senior Care Facility. One exception to this rule is for communities in which 50% or more of the units are independent living (IL) but the IL buildings are separately metered stand-alone buildings, a valid rating can be generated only by fully excluding the IL buildings from the rest of the campus. Facilities with more than 50% independent living units cannot earn an ENERGY STAR score and should benchmark using the Multifamily property type.
[15 empty] | Retail |  |  |  | Retail | [5 empty] | Retail Store refers to individual stores used to conduct the retail sale of non-food consumer goods such as clothing, books, toys, sporting goods, office supplies, hardware, and electronics. Buildings containing multiple stores should be classified as enclosed mall, lifestyle center, or strip mall. Gross Floor Area should include all space within the building(s), including sales areas, storage areas, offices staff break rooms, elevators, and stairwells. To receive an ENERGY STAR score, a Retail Store must be asingle store that is at least 5,000 square feet and has an exterior entrance to the public. The ENERGY STAR score applies to: Department Stores, Discount Stores, Supercenters, Warehouse Clubs, Drug Stores, Dollar Stores, Home Center/Hardware Stores, and Apparel/Specialty Stores (e.g. books, clothing, office products, toys, home goods, and electronics). Eligible store configurations include: free standing stores; stores located in open air or strip centers (a collection of attached stores with common areas that are not enclosed); and mall anchors. Retail configurations not eligible to receive an ENERGY STAR score include: enclosed malls; individual stores located within enclosed malls; lifestyle centers; strip malls; and individual stores that are part of a larger non- mall building (i.e. office or hotel). Convenience Stores, Automobile Dealerships, and Restaurants are not eligible to earn an ENERGY STAR score as Retail. Supermarkets are eligible for an ENERGY STAR score under the Supermarket property type. Note: In order to be eligible to earn ENERGY STAR certification, your building must be located in the US or its territories, or owned by the US government outside of the US.
[15 empty] | Retail (Auto Dealership) |  |  |  | Retail (Auto Dealership) | [5 empty] | Automobile Dealership refers to buildings used for the sale of new or used cars and light trucks. Gross Floor Area should include all space within the building(s), including sales floors, offices, conference rooms, vehicle service centers, parts storage areas, waiting rooms, staff break rooms, hallways, and stairwells. Gross Floor Area should not include any exterior spaces such as vehicle parking areas.
[15 empty] | Retail (Conv w Gas Stn) |  |  |  | Retail (Conv w Gas Stn) | [5 empty] | Convenience Store with Gas Station refers to buildings that are co-located with gas stations and are used for the sale of a limited range of items such as groceries, toiletries, newspapers, soft drinks, tobacco products, and other everyday items. Convenience Store with Gas Station may include space for vehicle servicing and repair. Gross Floor Area should include all space within the building(s), including sales floors, offices, staff break rooms, storage areas, and vehicle repair areas. Energy use associated with outside areas such as vehicle parking and gas filling areas should be included with the total energy use for the building(s), but the square footage associated with these outdoor areas should not be included in the Gross Floor Area.
[15 empty] | Retail (Convenience St) |  |  |  | Retail (Convenience St) | [5 empty] | Convenience Store without Gas Station refers to buildings used for the sale of a limited range of items such as groceries, toiletries, newspapers, soft drinks, tobacco products, and other everyday items, which are not co-located with a gas station. Gross Floor Area should include all space within the building(s), including sales floors, offices, staff break rooms, and storage areas. Conference facilities located within a Hotel should be included along with your Hotel property use details, rather than added as a separate Convention Center property use. Conference facilities primarily serving smaller meetings should be entered as Social/Meeting Hall.
[15 empty] | Retail (Lifestyle Ctr) |  |  |  | Retail (Lifestyle Ctr) | [5 empty] | Lifestyle Center refers to a mixed use commercial development that includes retail stores and leisure amenities, where individual retail stores typically contain an entrance accessible from the outside and are not connected by internal walkways. Lifestyle centers have an open air design, unlike traditional enclosed malls, and often include landscaped pedestrian areas, as well as streets and vehicle parking. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, residential areas, storage areas, staff break rooms, walkways, stairwells, and mechanical areas. Do not include any exterior spaces such as pedestrian walkways or vehicle parking areas.
[15 empty] | Retail (Mall - enclosed) |  |  |  | Retail (Mall - enclosed) | [5 empty] | Enclosed Mall refers to buildings that house multiple stores, often “anchored” by one or more department stores, and with interior walkways. Most stores will not have entrances accessible from outside, with the exception of the “anchor” stores. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, storage areas, staff break rooms, atriums, walkways, stairwells, and mechanical rooms.
[15 empty] | Retail (Repair: Car/Shoe) |  |  |  | Retail (Repair: Car/Shoe) | [5 empty] | Repair Services refers to buildings in which some type of repair service is provided. Examples include vehicle service or repair shops, shoe repair, jewelry repair, locksmiths, etc. Gross Floor Area should include all space within the building(s), including sales floors, repair areas, workshops, offices, parts storage areas, waiting rooms, staff break rooms, hallways, and stairwells.
[15 empty] | Retail (Strip Mall) |  |  |  | Retail (Strip Mall) | [5 empty] | Strip mall refers to buildings comprising more than one retail store, restaurant, or other business, in an open-air configuration where each establishment has an exterior entrance to the public and there are no internal walkways. Gross Floor Area should include all space within the building(s), including retail stores, offices, restaurants, storage areas, staff break rooms, and stairwells. Do not include any exterior spaces such as vehicle parking areas. Note that individual stores within strip malls may be eligible to receive an ENERGY STAR score if they are over 5,000 square feet in size and have an exterior entrance to the public.
[15 empty] | Retail (Supermkt/Groc) |  |  |  | Retail (Supermkt/Groc) | [5 empty] | Supermarket/Grocery Store refers to buildings used for the retail sale of primarily food and beverage products, and which may include small amounts of preparation and sale of ready-to-eat food. Buildings where the primary business is the on-site preparation and sale of ready-to-eat food should use one of the Restaurant property types. Gross Floor Area should include all space within the building(s), including the sales floor, offices, storage areas, kitchens, staff break rooms, and stairwells. Gross Floor Area should include all space within the building, including court/rink space, all concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells.
[15 empty] | Retail (Wholesale Club) |  |  |  | Retail (Wholesale Club) | [5 empty] | Wholesale Club/Supercenter refers to buildings used to conduct the retail sale of a wide variety of merchandise, typically in bulk quantities. Merchandise may include food, clothing, office supplies, furniture, electronics, books, sporting goods, toys, and hardware. Gross Floor Area should include all space within the building(s), including the sales floor, offices, storage areas, kitchens, staff break rooms, elevators, and stairwells.
[15 empty] | Self Storage Facility |  |  |  | Self Storage Facility | [5 empty] | Self-Storage Facility refers to buildings that are used for private storage. Typically, a single Self Storage Facility will contain a variety of individual units that are rented out for the purpose of storing personal belongings. Gross Floor Area should include all space within the building(s), including individual storage units, administrative offices, security and maintenance areas, mechanical rooms, hallways, stairways, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[15 empty] | Trans Terminal/Station |  |  |  | Trans Terminal/Station | [5 empty] | Transportation Terminal/Station applies to buildings used primarily for accessing public or private transportation. This includes train stations, bus stations, airports, and seaports. These terminals include areas for ticket purchases, and embarkation/disembarkation, and may also include public waiting areas with restaurants and other concessions. Gross Floor Area should include all space within the building(s), including boarding areas, waiting areas, administrative space, kitchens used by staff, lobbies, restaurants, cafeterias, stairways, atria, elevator shafts, and storage areas. This should not includeany exterior spaces associated with the terminals, such as drop-off areas, outdoor platforms, or outdoor loading docks/bays.
[15 empty] | Unknown (Core & Shell) |  |  |  | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
[15 empty] | Warehouse (Non-Refrig) |  |  |  | Warehouse (Non-Refrig) | [5 empty] | Non-Refrigerated Warehouse refers to unrefrigerated buildings that are used to store goods, manufactured products, merchandise or raw materials. Gross Floor Area should include all space within the building(s), including the main storage rooms, administrative office offices, lobbies, stairways, restrooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[15 empty] | Warehouse (Refrig) |  |  |  | Warehouse (Refrig) | [5 empty] | Refrigerated Warehouse refers to refrigerated buildings that are used to store perishable goods or merchandise under refrigeration at temperatures below 50 degrees Fahrenheit. Gross Floor Area should include all space within the building(s), which includes temperature-controlled areas, administrative offices, lobbies, stairways, restrooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[15 empty] | Worship Facility |  |  |  | Worship Facility | [5 empty] | Worship Facility refers to buildings that are used as places of worship. This includes churches, temples, mosques, synagogues, meetinghouses, or any other buildings that primarily function as a place of religious worship. Gross Floor Area should include all areas inside the building that includes the primary worship area, including food preparation, community rooms, classrooms, and supporting areas such as restrooms, storage areas, hallways, and elevator shafts. The ENERGY STAR score for Worship Facilities applies to buildings that function as the primary place of worship and not to other buildings that may be associated with a religious organization, such as living quarters, schools, or buildings used primarily for other community activities. To receive an ENERGY STAR score, a Worship facility must have at least 25 seats, but cannot have more than 4,000.
[15 empty] | Unknown (Core & Shell) |  |  |  | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
|  |  |  | Building Address | [9 empty] | 2203 ABERDEEN STREET
Tenancy Address
| POSSE Street Names | [9 empty] | TIPs Eligible Buildings (2007+ VBBL) | [6 empty] | BOMA BESt Buildings | [7 empty] | 90.1-2007 (+) Buildings (includes Rz projects)
[24 empty] | 0 |  |  |  |  | 0 |  |  | 0
| ABBOTT STREET | [16 empty] | 1001 Cambie Street | [7 empty] | 1 W HASTINGS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ABERDEEN STREET | [16 empty] | 100-1090 Homer STREET | [7 empty] | 1005 STATION STREET |  |  |  | No | 90.1-2001 | FALSE
| ADANAC STREET | [16 empty] | 1001-1085 Cambie Street | [7 empty] | 1007 KEEFER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ADERA STREET | [16 empty] | 1021 W Hastings Street | [7 empty] | 1009 HARWOOD STREET |  |  |  | Yes | 90.1-2007 | FALSE
| AEGEAN CRESCENT | [16 empty] | 1050 W Pender Street | [7 empty] | 1009 LAURIER AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| AISNE STREET | [16 empty] | 1055 Dunsmuir Street | [7 empty] | 101 E 2ND AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| ALAMEIN AVENUE | [16 empty] | 1055 W Hastings Street | [7 empty] | 1010 E 7TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ALBERNI STREET | [16 empty] | 1066 W Hastings Street | [7 empty] | 1015 DENMAN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ALBERTA STREET | [16 empty] | 1075 W Georgia STREET | [7 empty] | 1015 W 8TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| ALDER BAY COURT | [16 empty] | 1085 Cambie Street | [7 empty] | 1018 E 24TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ALDER BAY WALK | [16 empty] | 1090 Homer STREET | [7 empty] | 1018 PARK DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| ALDER CROSSING | [16 empty] | 1095 W Pender Street | [7 empty] | 1018 W 11TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ALDER STREET | [16 empty] | 1100 Melville STREET | [7 empty] | 1021 W HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ALEXANDER STREET | [16 empty] | 111 Dunsmuir Street | [7 empty] | 1027 VICTORIA DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| ALEXANDRA STREET | [16 empty] | 1138 Melville Street | [7 empty] | 1036 E 21ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ALGONQUIN MEWS | [16 empty] | 1185 W Georgia Street | [7 empty] | 1037 W KING EDWARD AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| ALICE STREET | [16 empty] | 1188 W Georgia Street | [7 empty] | 1040 W GEORGIA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ALMA STREET | [16 empty] | 1249 Granville Street | [7 empty] | 1045 ROBSON STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ALRT GENERAL | [16 empty] | 1285 W Pender Street | [7 empty] | 1045 W WATERFRONT ROAD |  |  |  | Yes | 90.1-2007 | FALSE
| ALVIN NAROD MEWS | [16 empty] | 133 Walter Hardwick Avenue | [7 empty] | 1047 DAVIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| AMBERLY PLACE | [16 empty] | 1380 Burrard Street | [7 empty] | 1062 W 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ANCASTER CRESCENT | [16 empty] | 1489 W Broadway | [7 empty] | 1069 ALBERNI STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ANDERSON STREET | [16 empty] | 1489/1497 W Broadway | [7 empty] | 1077 GREAT NORTHERN WAY |  |  |  | Yes | R90.1-2010 | FALSE
| ANGLER'S PLACE | [16 empty] | 1497 W Broadway | [7 empty] | 108 E 35TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ANGUS DRIVE | [16 empty] | 1508 W Broadway | [7 empty] | 1090 W PENDER STREET |  |  |  | Yes | R90.1-2010 | FALSE
| ANN STREET | [16 empty] | 1529 W Pender Street | [7 empty] | 110 SWITCHMEN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ANTWERP LANE | [16 empty] | 1529-1555 W Pender Street | [7 empty] | 1101 W 7TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ANZIO DRIVE | [16 empty] | 155 Walter Hardwick Avenue | [7 empty] | 1105 SEYMOUR STREET |  |  |  | Yes | 90.1-2010 | FALSE
| APPLEDALE PLACE | [16 empty] | 155-189 Walter Hardwick Avenue | [7 empty] | 1107 SEYMOUR STREET |  |  |  | Yes | R90.1-2010 | FALSE
| AQUA DRIVE | [16 empty] | 1555 W Pender Street | [7 empty] | 1107 W 7TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| AQUARIUS MEWS | [16 empty] | 1681 A Manitoba Street | [7 empty] | 1108 PENDRELL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| AQUITANIA PLACE | [16 empty] | 1681 A& B Manitoba Street | [7 empty] | 111 E 2ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ARBOR AVENUE | [16 empty] | 1681 B Manitoba Street | [7 empty] | 1111 RICHARDS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ARBUTUS DIVERSION | [16 empty] | 1681 Manitoba Street | [7 empty] | 1111 SEYMOUR STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ARBUTUS STREET | [16 empty] | 1755 W 14th Avenue | [7 empty] | 1112 W 15TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ARCHIMEDES STREET | [16 empty] | 1818 Cornwall Street | [7 empty] | 1115 SEYMOUR STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ARGYLE DRIVE | [16 empty] | 189 Walter Hardwick Avenue | [7 empty] | 1116 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ARGYLE STREET | [16 empty] | 200 Burrard Street | [7 empty] | 1121 SEYMOUR STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ARLINGTON STREET | [16 empty] | 200 Granville Street | [7 empty] | 1130 E Broadway |  |  |  | Yes | 90.1-2010 | FALSE
| ASCOT PLACE | [16 empty] | 2025 W Broadway | [7 empty] | 1133 HORNBY STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ASH CRESCENT | [16 empty] | 2225 W 41st Avenue | [7 empty] | 1133 MELVILLE STREET |  |  |  | Yes | R90.1-2010+22% | FALSE
| ASH STREET | [16 empty] | 2475 W Broadway | [7 empty] | 1134 BURRARD STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ASHBURN STREET | [16 empty] | 2475-2485 W Broadway | [7 empty] | 1151 W GEORGIA STREET |  |  |  | No | 90.1-2001 | FALSE
| ASPEN AVENUE | [16 empty] | 2485 W Broadway | [7 empty] | 1155 THURLOW STREET |  |  |  | Yes | R90.1-2010 | FALSE
| ATHLETES WAY | [16 empty] | 250 Howe Street | [7 empty] | 1157 E 14TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ATHLONE STREET | [16 empty] | 2611 Nootka Street | [7 empty] | 1161 PARKER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ATLANTIC STREET | [16 empty] | 2633 Nootka Street | [7 empty] | 1166 W 14TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ATLAS LANE | [16 empty] | 2910 Virtual Way | [7 empty] | 1168 PENDRELL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ATLIN STREET | [16 empty] | 2920 Virtual Way | [7 empty] | 1171 JERVIS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| AUBREY PLACE | [16 empty] | 2925 Virtual Way | [7 empty] | 1180 COMOX STREET |  |  |  | Yes | 90.1-2010 | FALSE
| AUSTREY AVENUE | [16 empty] | 2930 Virtual Way | [7 empty] | 1181 E 19TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| AVERY AVENUE | [16 empty] | 2940 Virtual Way | [7 empty] | 1188 BIDWELL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| AVISON WAY | [16 empty] | 2940 Virtual Way & 2945 Hebb | [7 empty] | 1205 HOWE STREET |  |  |  | No | 90.1-2001 | FALSE
| AVONDALE AVENUE | [16 empty] | 2945 Hebb Avenue | [7 empty] | 122 W 8TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BAILLIE STREET | [16 empty] | 2955 Hebb Avenue | [7 empty] | 1221 BIDWELL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BALACLAVA STREET | [16 empty] | 2955 Virtual Way | [7 empty] | 1223 E PENDER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BALDWIN STREET | [16 empty] | 2980 Virtual Way | [7 empty] | 123 W 16TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BALFOUR AVENUE | [16 empty] | 2980 Virtual Way / 2611 & 2633 Nootka Street / 2955 Hebb Avenue | [7 empty] | 1233 HOWE STREET |  |  |  | No | 90.1-2001 | FALSE
| BALKAN STREET | [16 empty] | 2985 Virtual Way | [7 empty] | 1233 W 75TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BALMORAL STREET | [16 empty] | 300 W Georgia Street | [7 empty] | 124 W 13TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BALSAM PLACE | [16 empty] | 3029 E Broadway | [7 empty] | 1253 W 75TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BALSAM STREET | [16 empty] | 3200 E 54th Avenue | [7 empty] | 1255 E 10TH AVENUE |  |  |  | No | 90.1-2001 | FALSE
| BARCLAY STREET | [16 empty] | 3283 E Broadway | [7 empty] | 1258 W BROADWAY |  |  |  | Yes | 90.1-2007 | FALSE
| BARNARD STREET | [16 empty] | 333 Seymour Street | [7 empty] | 1270 W 75TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BATTISON STREET | [16 empty] | 355 Burrard Street | [7 empty] | 1283 HOWE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BAUER STREET | [16 empty] | 3550 W Broadway | [7 empty] | 1289 HORNBY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BAYSHORE DRIVE | [16 empty] | 3625 Lougheed Highway | [7 empty] | 1289 W 76TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BAYSWATER STREET | [16 empty] | 401 Burrard Street | [7 empty] | 1290 E 11TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BEACH AVENUE | [16 empty] | 409 Granville Street | [7 empty] | 1301 JOHNSTON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BEACH CRESCENT | [16 empty] | 4750 Arbutus Street | [7 empty] | 1302 SEYMOUR STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BEADNELL COURT | [16 empty] | 50 W 2nd Avenue | [7 empty] | 1308 HORNBY STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BEAGLE COURT | [16 empty] | 505 Burrard Street | [7 empty] | 1310 RICHARDS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BEAMISH COURT | [16 empty] | 510 Burrard Street | [7 empty] | 1322 E 23RD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BEATRICE STREET | [16 empty] | 550 Burrard Street | [7 empty] | 1325 ROLSTON STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BEATTY STREET | [16 empty] | 555 Burrard Street | [7 empty] | 1328 E 23RD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BEATTY WALK | [16 empty] | 555 W Hastings Street | [7 empty] | 133 E 8TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BEECHWOOD STREET | [16 empty] | 580 Hornby Street | [7 empty] | 1335 HOWE STREET |  |  |  | Yes | R90.1-2010+22% | FALSE
| BEGG STREET | [16 empty] | 595 Burrard Street | [7 empty] | 1344 KINGSWAY |  |  |  | Yes | 90.1-2007 | FALSE
| BELLA-VISTA STREET | [16 empty] | 595 Howe Street | [7 empty] | 1350 KINGSWAY |  |  |  | Yes | 90.1-2007 | FALSE
| BELLEVUE DRIVE | [16 empty] | 601 W Cordova Street | [7 empty] | 1351 ADANAC STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BELMONT AVENUE | [16 empty] | 605 W Kent Avenue North | [7 empty] | 1351 CONTINENTAL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BENTALL STREET | [16 empty] | 625 Howe Street | [7 empty] | 1355 GARDEN DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| BENTLEY STREET | [16 empty] | 625 W Kent Avenue North | [7 empty] | 1360 E KENT AVENUE SOUTH |  |  |  | Yes | 90.1-2007 | FALSE
| BERING AVENUE | [16 empty] | 63 W 1st Avenue | [7 empty] | 1372 SEYMOUR STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BERKELEY STREET | [16 empty] | 63-75 W 1st Avenue | [7 empty] | 138 E 7TH AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| BEVERLY CRESCENT | [16 empty] | 650 W 41st Avenue | [7 empty] | 138 E HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BIDWELL STREET | [16 empty] | 650 W Georgia Street | [7 empty] | 138 W 1ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BIRCH STREET | [16 empty] | 655 W Kent Avenue North | [7 empty] | 1388 CONTINENTAL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BIRCH WALK | [16 empty] | 701 W Georgia STREET | [7 empty] | 1388 RICHARDS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BLAKE STREET | [16 empty] | 725 Granville STREET | [7 empty] | 1396 RICHARDS STREET |  |  |  | Yes | R90.1-2010 | FALSE
| BLANCA STREET | [16 empty] | 745 Thurlow Street | [7 empty] | 1405 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BLANCHE STREET | [16 empty] | 75 W 1st Avenue | [7 empty] | 1408 E 15TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BLAYDON COURT | [16 empty] | 789 W Pender Street | [7 empty] | 1408 E 41ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BLENHEIM STREET | [16 empty] | 800 Burrard Street | [7 empty] | 142 E PENDER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BLOOD ALLEY SQUARE | [16 empty] | 808 Nelson STREET | [7 empty] | 1450 VENABLES STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BLUE JAY CRESCENT | [16 empty] | 815 W Hastings Street | [7 empty] | 1460 BUTE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BOATHOUSE MEWS | [16 empty] | 850 W Hastings Street | [7 empty] | 1460 E HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BOATLIFT LANE | [16 empty] | 865 Hornby Street | [7 empty] | 1461 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BOBOLINK AVENUE | [16 empty] | 8755 Ash Street | [7 empty] | 1462 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BONACCORD DRIVE | [16 empty] | 8765 Ash Street | [7 empty] | 1480 HOWE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BONNYVALE AVENUE | [16 empty] | 885 W Georgia Street | [7 empty] | 1481 W 59TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BONSAI STREET | [16 empty] | 887 Great Northern Way | [7 empty] | 1488 W 58TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BORDEN STREET | [16 empty] | 888 Dunsmuir Street | [7 empty] | 1492 W 57TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BORHAM CRESCENT | [16 empty] | 890 W Pender Street | [7 empty] | 1495 ONTARIO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BOUNDARY ROAD | [16 empty] | 900 Howe Street | [7 empty] | 1499 W PENDER STREET |  |  |  | No | 90.1-2001 | FALSE
| BOYD DIVERSION | [16 empty] | 925 W Georgia Street | [7 empty] | 150 E CORDOVA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BRADFIELD COURT | [16 empty] | 930 Seymour Street | [7 empty] | 150 N RENFREW STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BRAEBURN STREET | [16 empty] | 939 Beatty Street | [7 empty] | 1507 W 59TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BRAHMS AVENUE | [16 empty] | 980 Howe STREET | [7 empty] | 1508 W 57TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BRAKENRIDGE STREET | [16 empty] | 980 Seymour STREET | [7 empty] | 151 W HASTINGS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BRANDYWINE PLACE | [16 empty] | 999 W Hastings Street | [7 empty] | 1510 VENABLES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BRANT STREET | [24 empty] | 1510 W 6TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BRIAR AVENUE | [24 empty] | 1515 W 57TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BRIDGEWAY | [24 empty] | 1515 W 7TH AVENUE |  |  |  | No | 90.1-2001 | FALSE
| BRIGADOON AVENUE | [24 empty] | 1529 COMOX STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BRIGHTWOOD PLACE | [24 empty] | 1534 HENSHAW LANE |  |  |  | Yes | 90.1-2010 | FALSE
| BROCK STREET | [24 empty] | 1539 Comox STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BROOKS STREET | [24 empty] | 1539 COMOX STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BROUGHTON STREET | [24 empty] | 155 E 37TH AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| BRUCE STREET | [24 empty] | 1550 ALBERNI STREET |  |  |  | Yes | R90.1-2010+22% | FALSE
| BRULE MEWS | [24 empty] | 1551 HENSHAW LANE |  |  |  | Yes | 90.1-2010 | FALSE
| BRUNSWICK STREET | [24 empty] | 1551 QUEBEC STREET |  |  |  | Yes | 90.1-2010 | FALSE
| BUCKETWHEEL | [24 empty] | 1551 W 57TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BURKHOLDER DRIVE | [24 empty] | 1555 W 8TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BURNABY STREET | [24 empty] | 1561 W 57TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BURQUITLAM DRIVE | [24 empty] | 1565 W 6TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BURRARD STREET | [24 empty] | 1571 W 57TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| BURSILL STREET | [24 empty] | 1575 W 6TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BUSCOMBE STREET | [24 empty] | 1588 E HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| BUTE STREET | [24 empty] | 1598 SE MARINE DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| BUTLER STREET | [24 empty] | 1601 W 7TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| BYWELL COURT | [24 empty] | 161 E 1ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CAMANO STREET | [24 empty] | 161 W 14TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CAMBIE STREET | [24 empty] | 1618 QUEBEC STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CAMBRIDGE STREET | [24 empty] | 1618 W 6TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CAMERON AVENUE | [24 empty] | 1623 PANDORA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CAMOSUN STREET | [24 empty] | 1625 W 3RD AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CAMPBELL AVENUE | [24 empty] | 1628 E 21ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CANADA PLACE | [24 empty] | 1628 W 4TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CAPRI CRESCENT | [24 empty] | 1635 W 3RD AVENUE |  |  |  | No | 90.1-2001 | FALSE
| CAPTAIN'S COVE | [24 empty] | 1647 E PENDER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CARDERO STREET | [24 empty] | 1648 FRANCES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CARIBOO STREET | [24 empty] | 1650 W 2ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CARLISLE STREET | [24 empty] | 1661 DAVIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CARNARVON STREET | [24 empty] | 1661 QUEBEC STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CAROLINA STREET | [24 empty] | 1668 DAVIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CARRALL STREET | [24 empty] | 1669 E BROADWAY |  |  |  | No | 90.1-2001 | FALSE
| CARRINGTON STREET | [24 empty] | 167 W 14TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CARTIER PLACE | [24 empty] | 1675 W 3RD AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CARTIER STREET | [24 empty] | 1678 PULLMAN PORTER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CARTWRIGHT STREET | [24 empty] | 168 E 35TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CASSIAR CONNECTOR | [24 empty] | 168 W 1ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CASSIAR RUPERT DIVERSION | [24 empty] | 1685 ONTARIO STREET |  |  |  | No | 90.1-2001 | FALSE
| CASSIAR STREET | [24 empty] | 1688 PULLMAN PORTER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CAVERSHAM COURT | [24 empty] | 1689 E 13TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CECIL STREET | [24 empty] | 169 W 7TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CEDAR COTTAGE MEWS | [24 empty] | 1691 JOHNSTON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CEDAR CRESCENT | [24 empty] | 1708 ONTARIO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CEDARHURST STREET | [24 empty] | 1720 KINGSWAY |  |  |  | Yes | 90.1-2010 | FALSE
| CELISTA DRIVE | [24 empty] | 1723 VICTORIA DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| CELTIC AVENUE | [24 empty] | 1723 Victoria STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CENTENNIAL ROAD | [24 empty] | 1723 W 4TH AVENUE |  |  |  | No | 90.1-2001 | FALSE
| CENTRAL STREET | [24 empty] | 1755 W 14TH AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| CHALDECOTT STREET | [24 empty] | 1768 COOK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CHAMBERS STREET | [24 empty] | 177 ROBSON STREET |  |  |  | No | 90.1-2001 | FALSE
| CHAMBORD PLACE | [24 empty] | 1770 Pendrell STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CHAMPLAIN CRESCENT | [24 empty] | 1775 QUEBEC STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CHANDLERY PLACE | [24 empty] | 1777 W 7TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CHARLES STREET | [24 empty] | 1783 MANITOBA STREET |  |  |  | Yes | R90.1-2010 | FALSE
| CHARLESON | [24 empty] | 1785 W 4TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CHATEAU PLACE | [24 empty] | 1788 COLUMBIA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CHATHAM STREET | [24 empty] | 1788 ONTARIO STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CHEAM PLACE | [24 empty] | 1788 W 2ND AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CHERRY STREET | [24 empty] | 179 MAIN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CHESS STREET | [24 empty] | 1790 BEACH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CHESTER STREET | [24 empty] | 1796 PANDORA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CHESTNUT STREET | [24 empty] | 180 SWITCHMEN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CHEYENNE AVENUE | [24 empty] | 180 W 63RD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CHICKADEE PLACE | [24 empty] | 1808 W 3RD AVENUE |  |  |  | No | 90.1-2001 | FALSE
| CHILCO STREET | [24 empty] | 1819 VICTORIA DIVERSION |  |  |  | Yes | 90.1-2007 | FALSE
| CHOY YUEN CRESCENT | [24 empty] | 1819 W 5TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CHURCH STREET | [24 empty] | 183 E GEORGIA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CHURCHILL STREET | [24 empty] | 1838 RENFREW STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CITADEL PARADE | [24 empty] | 1838 W 12TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CITY EDGE PLACE | [24 empty] | 1843 ADANAC STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CLANCY LORANGER WAY | [24 empty] | 1860 BURRARD STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CLARENDON STREET | [24 empty] | 1865 ADANAC STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CLARK DRIVE | [24 empty] | 1872 PARKER STREET |  |  |  | Yes | R90.1-2010+22% | FALSE
| CLEADON COURT | [24 empty] | 188 E 1ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CLERMONT MEWS | [24 empty] | 188 E 49TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CLIVE AVENUE | [24 empty] | 188 KEEFER STREET |  |  |  | Yes | R90.1-2010 | FALSE
| COAL HARBOUR QUAY | [24 empty] | 1880 FRANCES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| COAL HARBOUR ROAD | [24 empty] | 1880 RENFREW STREET |  |  |  | Yes | R90.1-2010 | FALSE
| COBBLESTONE AVENUE | [24 empty] | 1889 TRIUMPH STREET |  |  |  | Yes | 90.1-2007 | FALSE
| COLERIDGE AVENUE | [24 empty] | 189 KEEFER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| COLFAX CRESCENT | [24 empty] | 1890 SKEENA STREET |  |  |  | Yes | R90.1-2010 | FALSE
| COLLEGE STREET | [24 empty] | 1890 SPYGLASS PLACE |  |  |  | No | 90.1-2001 | FALSE
| COLLINGWOOD PLACE | [24 empty] | 191 E 11TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| COLLINGWOOD STREET | [24 empty] | 191 E 57TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| COLUMBIA STREET | [24 empty] | 1910 FERNDALE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| COMMERCIAL DIVERSION NORTH | [24 empty] | 1918 POWELL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| COMMERCIAL DRIVE | [24 empty] | 1919 WYLIE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| COMMERCIAL STREET | [24 empty] | 1920 SW MARINE DRIVE |  |  |  | Yes | R90.1-2010 | FALSE
| COMMISSIONER STREET | [24 empty] | 1989 E 36TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| COMMODORE ROAD | [24 empty] | 2005 QUEBEC STREET |  |  |  | Yes | 90.1-2010 | FALSE
| COMOX STREET | [24 empty] | 2008 E 54TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CONNAUGHT DRIVE | [24 empty] | 2009 E HASTINGS STREET |  |  |  | No | 90.1-2001 | FALSE
| CONTINENTAL STREET | [24 empty] | 2010 GLEN DRIVE |  |  |  | No | 90.1-2001 | FALSE
| COOK STREET | [24 empty] | 202 E 24TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| COOPERAGE WAY | [24 empty] | 2020 ALMA STREET |  |  |  | No | 90.1-2001 | FALSE
| COOPERATIVE WAY | [24 empty] | 2020 ARBUTUS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| COOPER'S MEWS | [24 empty] | 2034 FRANKLIN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| COPELAND AVENUE | [24 empty] | 2035 W 4TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| COPLEY STREET | [24 empty] | 2080 COMMERCIAL DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| COQUIHALLA DRIVE | [24 empty] | 2080 Commercial STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CORAL REEF PLACE | [24 empty] | 2080 W BROADWAY |  |  |  | Yes | 90.1-2007 | FALSE
| CORDIALE DRIVE | [24 empty] | 2089 W 43RD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CORDOVA DIVERSION | [24 empty] | 209 E 7TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CORNERSTONE STREET | [24 empty] | 2095 W 43RD AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| CORNETT ROAD | [24 empty] | 2095 W 44TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CORNISH STREET | [24 empty] | 210 E 5TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CORNWALL AVENUE | [24 empty] | 2101 W 4TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CORSICA WAY | [24 empty] | 2102 W 48TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| COTTON DRIVE | [24 empty] | 2110 ETON STREET |  |  |  | Yes | 90.1-2007 | FALSE
| COTTRELL STREET | [24 empty] | 2118 W 15TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| COUILLARD MEWS | [24 empty] | 2121 ALDER CROSSING |  |  |  | Yes | 90.1-2007 | FALSE
| COURTENAY STREET | [24 empty] | 2128 W 40TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CRANBERRY DRIVE | [24 empty] | 2141 E HASTINGS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CREE STREET | [24 empty] | 215 E 33RD AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CREEKSIDE DRIVE | [24 empty] | 215 MAIN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| CREELMAN AVENUE | [24 empty] | 215 W 2ND AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CRESSWELL COURT | [24 empty] | 2150 BRIGADOON AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CROMPTON STREET | [24 empty] | 2150 E HASTINGS STREET |  |  |  | No | 90.1-2001 | FALSE
| CROMWELL STREET | [24 empty] | 2154 W 7TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CROWE STREET | [24 empty] | 218 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CROWLEY DRIVE | [24 empty] | 219 E GEORGIA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| CROWN CRESCENT | [24 empty] | 22 E 5th AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CROWN STREET | [24 empty] | 220 PRINCESS AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| CULLODEN STREET | [24 empty] | 220 TERMINAL AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CURATE WYND | [24 empty] | 220 VICTORIA DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| CYPRESS CRESCENT | [24 empty] | 220 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| CYPRESS STREET | [24 empty] | 2206 CLARK DRIVE |  |  |  | Yes | 90.1-2007 | FALSE
| DARTMOOR PLACE | [24 empty] | 221 UNION STREET |  |  |  | No | 90.1-2001 | FALSE
| DAVIE STREET | [24 empty] | 2211 CAMBIE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| DAWSON STREET | [24 empty] | 2215 E HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| DEASE LANE | [24 empty] | 222 E 30TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| DEERING ISLAND PLACE | [24 empty] | 2220 KINGSWAY |  |  |  | Yes | R90.1-2010 | FALSE
| DENMAN STREET | [24 empty] | 2233 COLUMBIA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| DEVONSHIRE CRESCENT | [24 empty] | 2239 KINGSWAY |  |  |  | Yes | 90.1-2007 | FALSE
| DIEPPE DRIVE | [24 empty] | 2239 W 7TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| DIEPPE PLACE | [24 empty] | 225 SMITHE STREET |  |  |  | Yes | R90.1-2010+22% | FALSE
| DINMONT AVENUE | [24 empty] | 2255 W 10TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| DISCOVERY STREET | [24 empty] | 2261 W 41ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| DOGWOOD AVENUE | [24 empty] | 2268 BAYSWATER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| DOMAN STREET | [24 empty] | 2290 MAIN STREET |  |  |  | Yes | R90.1-2010 | FALSE
| DONCASTER WAY | [24 empty] | 2298 GALT STREET |  |  |  | Yes | R90.1-2010 | FALSE
| DOUGLAS CRESCENT | [24 empty] | 2301 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| DRAKE STREET | [24 empty] | 231 E PENDER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| DRUMMOND DRIVE | [24 empty] | 232 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| DUCHESS STREET | [24 empty] | 2328 Galt STREET |  |  |  | Yes | 90.1-2010 | FALSE
| DUDLEY STREET | [24 empty] | 233 KINGSWAY |  |  |  | Yes | 90.1-2010 | FALSE
| DUFF STREET | [24 empty] | 2333 W 41ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| DUKE STREET | [24 empty] | 2355 E 30TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| DUMFRIES STREET | [24 empty] | 238 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| DUNBAR DIVERSION | [24 empty] | 238 W BROADWAY |  |  |  | Yes | 90.1-2010 | FALSE
| DUNBAR STREET | [24 empty] | 2384 E 34TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| DUNDAS STREET | [24 empty] | 2408 E BROADWAY |  |  |  | Yes | 90.1-2007 | FALSE
| DUNDEE STREET | [24 empty] | 242 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| DUNELM AVENUE | [24 empty] | 2426 W 8TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| DUNKIRK STREET | [24 empty] | 2435 W BROADWAY |  |  |  | Yes | 90.1-2010 | FALSE
| DUNLEVY AVENUE | [24 empty] | 2439 W 5TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| DUNSMUIR STREET | [24 empty] | 245 E GEORGIA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| DUNSMUIR VIADUCT | [24 empty] | 2462 GRANDVIEW HIGHWAY SOUTH |  |  |  | Yes | 90.1-2007 | FALSE
| DURANLEAU STREET | [24 empty] | 2465 FRASER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| DURWARD AVENUE | [24 empty] | 2468 BALACLAVA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 1ST AVENUE | [24 empty] | 2468 BAYSWATER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 2ND AVENUE | [24 empty] | 2475 CROWN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 3RD AVENUE | [24 empty] | 2477 CAROLINA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 4TH AVENUE | [24 empty] | 2481 WATERLOO STREET |  |  |  | No | 90.1-2001 | FALSE
| E 5TH AVENUE | [24 empty] | 2509 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 6TH AVENUE | [24 empty] | 2511 QUEBEC STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 7TH AVENUE | [24 empty] | 252 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 8TH AVENUE | [24 empty] | 2525 CARNARVON STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 10TH AVENUE | [24 empty] | 2528 COLLINGWOOD STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 11TH AVENUE | [24 empty] | 2528 MAPLE STREET |  |  |  | No | 90.1-2001 | FALSE
| E 12TH AVENUE | [24 empty] | 2549 CORNWALL AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E 13TH AVENUE | [24 empty] | 2550 SPRUCE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 14TH AVENUE | [24 empty] | 2565 MAPLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 15TH AVENUE | [24 empty] | 26 E 1ST AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| E 16TH AVENUE | [24 empty] | 260 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 17TH AVENUE | [24 empty] | 260 W 70TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 18TH AVENUE | [24 empty] | 2601 E 37TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 19TH AVENUE | [24 empty] | 2601 E 43RD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 20TH AVENUE | [24 empty] | 2610 VICTORIA DRIVE |  |  |  | Yes | R90.1-2010 | FALSE
| E 21ST AVENUE | [24 empty] | 262 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 22ND AVENUE | [24 empty] | 2625 E 43RD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 23RD AVENUE | [24 empty] | 2625 LAKEWOOD DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| E 24TH AVENUE | [24 empty] | 265 E 4TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 25TH AVENUE | [24 empty] | 266 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 26TH AVENUE | [24 empty] | 2687 MAPLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 27TH AVENUE | [24 empty] | 2689 KINGSWAY |  |  |  | Yes | 90.1-2007 | FALSE
| E 28TH AVENUE | [24 empty] | 2706 TRAFALGAR STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 29TH AVENUE | [24 empty] | 2706 W 2ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 30TH AVENUE | [24 empty] | 2711 KINGSWAY |  |  |  | Yes | 90.1-2007 | FALSE
| E 31ST AVENUE | [24 empty] | 2717 HORLEY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 32ND AVENUE | [24 empty] | 2721 GRANVILLE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 33RD AVENUE | [24 empty] | 2723 GRANVILLE STREET |  |  |  | No | 90.1-2001 | FALSE
| E 34TH AVENUE | [24 empty] | 2727 WARD STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 35TH AVENUE | [24 empty] | 2739 WARD STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 36TH AVENUE | [24 empty] | 274 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 37TH AVENUE | [24 empty] | 2745 E HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 38TH AVENUE | [24 empty] | 2750 E HASTINGS STREET |  |  |  | No | 90.1-2001 | FALSE
| E 39TH AVENUE | [24 empty] | 2750 SE MARINE DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| E 40TH AVENUE | [24 empty] | 2757 HORLEY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 41ST AVENUE | [24 empty] | 276 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 42ND AVENUE | [24 empty] | 2761 DUKE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 43RD AVENUE | [24 empty] | 2768 KINGSWAY |  |  |  | Yes | R90.1-2010 | FALSE
| E 44TH AVENUE | [24 empty] | 2777 E KENT AVENUE NORTH |  |  |  | Yes | 90.1-2010 | FALSE
| E 45TH AVENUE | [24 empty] | 2778 E HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 46TH AVENUE | [24 empty] | 2788 PRINCE EDWARD STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 47TH AVENUE | [24 empty] | 2790 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 48TH AVENUE | [24 empty] | 2805 E HASTINGS STREET |  |  |  | Yes | R90.1-2010+22% | FALSE
| E 49TH AVENUE | [24 empty] | 2817 CLARK DRIVE |  |  |  | No | 90.1-2001 | FALSE
| E 50TH AVENUE | [24 empty] | 2833 E KENT AVENUE NORTH |  |  |  | Yes | 90.1-2010 | FALSE
| E 51ST AVENUE | [24 empty] | 285 E 10TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 52ND AVENUE | [24 empty] | 2858 W 4TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E 53RD AVENUE | [24 empty] | 288 E HASTINGS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 54TH AVENUE | [24 empty] | 288 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 55TH AVENUE | [24 empty] | 2880 VENABLES STREET |  |  |  | No | 90.1-2001 | FALSE
| E 56TH AVENUE | [24 empty] | 2888 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 57TH AVENUE | [24 empty] | 2888 E 2ND AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E 58TH AVENUE | [24 empty] | 2888 GRANVILLE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 59TH AVENUE | [24 empty] | 2889 E 12TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E 60TH AVENUE | [24 empty] | 2889 E 1ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| E 61ST AVENUE | [24 empty] | 289 E 6TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E 62ND AVENUE | [24 empty] | 2906 W 33RD AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E 63RD AVENUE | [24 empty] | 2922 E KENT AVENUE SOUTH |  |  |  | Yes | 90.1-2010 | FALSE
| E 64TH AVENUE | [24 empty] | 295 E 1ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E 65TH AVENUE | [24 empty] | 2968 BIRCH STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 66TH AVENUE | [24 empty] | 2975 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E 67TH AVENUE | [24 empty] | 2980 NANAIMO STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 68TH AVENUE | [24 empty] | 3028 ARBUTUS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E 69TH AVENUE | [24 empty] | 303 E PENDER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E BROADWAY | [24 empty] | 305 W 41ST AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| E CORDOVA STREET | [24 empty] | 306 TERMINAL AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E GEORGIA STREET | [24 empty] | 3070 COMMERCIAL DRIVE |  |  |  | No | 90.1-2001 | FALSE
| E HASTINGS STREET | [24 empty] | 308 W HASTINGS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| E KENT AVENUE NORTH | [24 empty] | 3080 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E KENT AVENUE SOUTH | [24 empty] | 3080 MANITOBA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| E KING EDWARD AVENUE | [24 empty] | 3088 CELTIC AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E PENDER STREET | [24 empty] | 3089 W 3RD AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| E WATERFRONT ROAD | [24 empty] | 3090 E 54TH AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| E WOODSTOCK AVENUE | [24 empty] | 3090 ROSEMONT DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| EARL FINNING WAY | [24 empty] | 31 W PENDER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| EARLES STREET | [24 empty] | 3108 CELTIC AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| EAST BOULEVARD | [24 empty] | 311 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ECHO PLACE | [24 empty] | 311 E 6TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| EDDINGTON DRIVE | [24 empty] | 3140 W 57TH AVENUE |  |  |  | No | 90.1-2001 | FALSE
| EDGAR CRESCENT | [24 empty] | 3150 COMMERCIAL DRIVE |  |  |  | Yes | 90.1-2007 | FALSE
| EDINBURGH STREET | [24 empty] | 3155 KINGSWAY |  |  |  | Yes | 90.1-2007 | FALSE
| EIHU LANE | [24 empty] | 3161 QUEBEC STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ELDORADO MEWS | [24 empty] | 3183 PIERVIEW CRESCENT |  |  |  | Yes | 90.1-2010 | FALSE
| ELGIN STREET | [24 empty] | 320 GRANVILLE STREET |  |  |  | Yes | R90.1-2010 | FALSE
| ELIZABETH STREET | [24 empty] | 321 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ELK VALLEY PLACE | [24 empty] | 322 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ELLIOTT STREET | [24 empty] | 3245 PIERVIEW CRESCENT |  |  |  | Yes | 90.1-2010 | FALSE
| ELM STREET | [24 empty] | 325 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ELMHURST DRIVE | [24 empty] | 3250 MARINE WAY |  |  |  | Yes | 90.1-2010 | FALSE
| ETON STREET | [24 empty] | 3263 PIERVIEW CRESCENT |  |  |  | Yes | 90.1-2010 | FALSE
| EUCLID AVENUE | [24 empty] | 3268 MARINE WAY |  |  |  | Yes | 90.1-2010 | FALSE
| EVANS AVENUE | [24 empty] | 3281 E KENT AVENUE NORTH |  |  |  | Yes | 90.1-2010 | FALSE
| EVELEIGH STREET | [24 empty] | 3288 E 22ND AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| EXPLORERS WALK | [24 empty] | 3289 RIVERWALK AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| EXPO BOULEVARD | [24 empty] | 3289 Riverwalk STREET |  |  |  | Yes | 90.1-2010 | FALSE
| FAIRCHILD ROAD | [24 empty] | 329 E 7TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FAIRMONT STREET | [24 empty] | 3311 E HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| FALAISE AVENUE | [24 empty] | 333 E 11TH AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| FALAISE PLACE | [24 empty] | 333 WOODLAND DRIVE |  |  |  | Yes | 90.1-2007 | FALSE
| FALSE CREEK TRAM | [24 empty] | 3333 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| FANNIN AVENUE | [24 empty] | 3351 W 4TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| FELLOWES STREET | [24 empty] | 3352 SW MARINE DRIVE |  |  |  | No | 90.1-2001 | FALSE
| FERNDALE STREET | [24 empty] | 336 W 14TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| FERRY ROW | [24 empty] | 336 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FIELDSTONE AVENUE | [24 empty] | 3360 VICTORIA DRIVE |  |  |  | No | 90.1-2001 | FALSE
| FINCH PLACE | [24 empty] | 3365 E 4TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FINDLAY STREET | [24 empty] | 337 W PENDER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| FIR STREET | [24 empty] | 338 W 64TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FLAGSTAFF PLACE | [24 empty] | 34 W 7th AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FLEMING STREET | [24 empty] | 3410 LOUGHEED HIGHWAY |  |  |  | No | 90.1-2001 | FALSE
| FOLEY STREET | [24 empty] | 3420 ST. CATHERINES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| FORESHORE WALK | [24 empty] | 3437 KINGSWAY |  |  |  | Yes | 90.1-2007 | FALSE
| FORGE WALK | [24 empty] | 3456 COMMERCIAL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| FOSTER AVENUE | [24 empty] | 3488 SAWMILL CRESCENT |  |  |  | Yes | 90.1-2010 | FALSE
| FOUNDRY QUAY | [24 empty] | 349 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FOUNTAIN WAY | [24 empty] | 3496 MONS DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| FOUNTAIN WAY COURT | [24 empty] | 3505 GRANDVIEW HIGHWAY |  |  |  | Yes | 90.1-2007 | FALSE
| FOXHOUND MEWS | [24 empty] | 352 W 62ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FRANCES STREET | [24 empty] | 353 RAILWAY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| FRANKLIN STREET | [24 empty] | 355 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FRASER STREET | [24 empty] | 3550 LOUGHEED HIGHWAY |  |  |  | Yes | 90.1-2007 | FALSE
| FRASERVIEW DRIVE | [24 empty] | 3590 CORNETT ROAD |  |  |  | Yes | 90.1-2007 | FALSE
| FREDERICK STREET | [24 empty] | 3592 W 29TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FREMLIN STREET | [24 empty] | 3593 W 30TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| FRENCH STREET | [24 empty] | 3595 W 17TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| FRONTENAC STREET | [24 empty] | 3599 HULL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GALIANO ROAD | [24 empty] | 3603 W 27TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GALT STREET | [24 empty] | 3618 SAWMILL CRESCENT |  |  |  | Yes | 90.1-2010 | FALSE
| GAOLER'S MEWS | [24 empty] | 3624 MAIN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| GARDEN DRIVE | [24 empty] | 3625 E 1ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GARIBALDI DRIVE | [24 empty] | 365 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GASTON STREET | [24 empty] | 3659 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GATINEAU PLACE | [24 empty] | 3665 LOUGHEED HIGHWAY |  |  |  | Yes | 90.1-2007 | FALSE
| GEORGE STREET | [24 empty] | 3666 SAWMILL CRESCENT |  |  |  | Yes | 90.1-2010 | FALSE
| GEORGIA VIADUCT | [24 empty] | 3669 W 11TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GHENT LANE | [24 empty] | 368 W 64TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GILFORD STREET | [24 empty] | 3688 INVERNESS STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GILLNET PLACE | [24 empty] | 3688 SAWMILL CRESCENT |  |  |  | Yes | 90.1-2010 | FALSE
| GLADSTONE STREET | [24 empty] | 3699 MARINE WAY |  |  |  | Yes | 90.1-2010 | FALSE
| GLEN DRIVE | [24 empty] | 3736 COMMERCIAL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GLENDALE STREET | [24 empty] | 375 W 59TH AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| GLENDALOUGH PLACE | [24 empty] | 378 W 64TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GLENGYLE STREET | [24 empty] | 379 E BROADWAY |  |  |  | Yes | 90.1-2010 | FALSE
| GOLDEN LINK CRESCENT | [24 empty] | 3795 COMMERCIAL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| GORE AVENUE | [24 empty] | 38 W 1ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| GOTHARD STREET | [24 empty] | 380 W 5TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GRANDVIEW HIGHWAY | [24 empty] | 3800 FLEMING STREET |  |  |  | Yes | 90.1-2010 | FALSE
| GRANDVIEW HIGHWAY NORTH | [24 empty] | 3821 POINT GREY ROAD |  |  |  | Yes | 90.1-2010 | FALSE
| GRANDVIEW HIGHWAY SOUTH | [24 empty] | 3835 MAIN STREET |  |  |  | No | 90.1-2001 | FALSE
| GRANT STREET | [24 empty] | 388 KASLO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| GRANVILLE STREET | [24 empty] | 388 KOOTENAY STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GRAVELEY STREET | [24 empty] | 388 SKEENA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| GREAT NORTHERN WAY | [24 empty] | 388 W 64TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| GREENCHAIN | [24 empty] | 3891 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GREENSBORO PLACE | [24 empty] | 39 SMITHE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| GREER AVENUE | [24 empty] | 3917 KNIGHT STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GRIFFITHS WAY | [24 empty] | 3939 KNIGHT STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GROUSE WALK | [24 empty] | 3950 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GUELPH STREET | [24 empty] | 3951 NANAIMO STREET |  |  |  | Yes | 90.1-2007 | FALSE
| GWILLIM CRESCENT | [24 empty] | 4050 ASH STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HAGGART STREET | [24 empty] | 4060 YUKON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HAIDA DRIVE | [24 empty] | 4070 YUKON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HAIG STREET | [24 empty] | 4080 YUKON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HAILSTONE STREET | [24 empty] | 4083 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HALSS CRESCENT | [24 empty] | 4099 CAMBIE STREET |  |  |  | Yes | R90.1-2010 | FALSE
| HAMILTON STREET | [24 empty] | 41 E HASTINGS STREET |  |  |  | Yes | R90.1-2010 | FALSE
| HANDEL AVENUE | [24 empty] | 4103 BRANT STREET |  |  |  | Yes | 90.1-2007 | FALSE
| HARO STREET | [24 empty] | 4135 W 8TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| HAROLD STREET | [24 empty] | 415 E 6TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| HARRIET STREET | [24 empty] | 4150 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HARRISON DRIVE | [24 empty] | 4171 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HARWOOD STREET | [24 empty] | 4175 W 29TH AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| HAWKS AVENUE | [24 empty] | 4177 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HAZELTON STREET | [24 empty] | 4189 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HEATHER STREET | [24 empty] | 420 HAWKS AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| HEATLEY AVENUE | [24 empty] | 425 INDUSTRIAL AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| HEBB AVENUE | [24 empty] | 431 VERNON DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| HECATE PLACE | [24 empty] | 4320 SLOCAN STREET |  |  |  | Yes | R90.1-2010 | FALSE
| HELMCKEN STREET | [24 empty] | 433 SW MARINE DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| HEMLOCK COURT | [24 empty] | 433 VERNON DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| HEMLOCK STREET | [24 empty] | 4330 KNIGHT STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HENNEPIN AVENUE | [24 empty] | 4338 COMMERCIAL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| HENRY STREET | [24 empty] | 4348 KNIGHT STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HENSHAW LANE | [24 empty] | 4355 W 10TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| HERMON DRIVE | [24 empty] | 4372 FRASER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| HERON PLACE | [24 empty] | 438 TERMINAL AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| HIGH ROAD | [24 empty] | 438 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| HIGHBURY STREET | [24 empty] | 4400 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HIGHGATE STREET | [24 empty] | 4408 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HOLLAND STREET | [24 empty] | 4418 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HOLLYHOCK LANE | [24 empty] | 4427 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HOMER MEWS | [24 empty] | 445 KINGSWAY |  |  |  | Yes | R90.1-2010+22% | FALSE
| HOMER STREET | [24 empty] | 445 SE MARINE DRIVE |  |  |  | Yes | R90.1-2010 | FALSE
| HORLEY STREET | [24 empty] | 445 W 2ND AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| HORNBY STREET | [24 empty] | 4478 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HOSMER AVENUE | [24 empty] | 4488 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HOWE STREET | [24 empty] | 450 GORE AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| HOY STREET | [24 empty] | 450 SW MARINE DRIVE |  |  |  | Yes | 90.1-2007 | FALSE
| HOYLAKE AVENUE | [24 empty] | 4500 OAK STREET |  |  |  | Yes | R90.1-2010 | FALSE
| HUDSON STREET | [24 empty] | 4513 NANAIMO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HULL STREET | [24 empty] | 4515 NANAIMO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HUM-LU-SUM DRIVE | [24 empty] | 4519 EARLES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HUMM STREET | [24 empty] | 455 SW MARINE DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| HUMMINGBIRD PLACE | [24 empty] | 4550 FRASER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| HURON MEWS | [24 empty] | 4567 HEATHER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| HURST AVENUE | [24 empty] | 4573 SLOCAN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HURST PLACE | [24 empty] | 4575 SLOCAN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| HYACK DRIVE | [24 empty] | 4577 SLOCAN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| INDUSTRIAL AVENUE | [24 empty] | 458 E 10TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| INTERURBAN WAY | [24 empty] | 460 E KENT AVENUE SOUTH |  |  |  | Yes | 90.1-2007 | FALSE
| INVERNESS STREET | [24 empty] | 4650 GLADSTONE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| IRONWORK PASSAGE | [24 empty] | 467 W KING EDWARD AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| ISABEL PLACE | [24 empty] | 468 TERMINAL AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| ISLAND AVENUE | [24 empty] | 4698 OAK STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ISLAND PARK WALK | [24 empty] | 4773 BELMONT AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| IVANHOE STREET | [24 empty] | 481 W 26TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| JACK UPPAL STREET | [24 empty] | 4815 ELDORADO MEWS |  |  |  | Yes | 90.1-2007 | FALSE
| JACKSON AVENUE | [24 empty] | 4818 ELDORADO MEWS |  |  |  | Yes | 90.1-2007 | FALSE
| JADETREE COURT | [24 empty] | 4818 WILLOW STREET |  |  |  | Yes | 90.1-2007 | FALSE
| JAMES STREET | [24 empty] | 4867 CAMBIE STREET |  |  |  | Yes | R90.1-2010 | FALSE
| JAMES WALK | [24 empty] | 488 POWELL STREET |  |  |  | Yes | 90.1-2007 | FALSE
| JASPER CRESCENT | [24 empty] | 489 W 26TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| JELLICOE STREET | [24 empty] | 490 W 64TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| JEPSON-YOUNG LANE | [24 empty] | 4951 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| JERICHO CIRCLE | [24 empty] | 496 DRAKE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| JERICHO DRIVE | [24 empty] | 4963 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| JERVIS MEWS | [24 empty] | 4988 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| JERVIS STREET | [24 empty] | 499 PACIFIC STREET |  |  |  | Yes | 90.1-2010 | FALSE
| JOHN STREET | [24 empty] | 5002 HIGHGATE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| JOHNSTON STREET | [24 empty] | 501 E 44TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| JOYCE STREET | [24 empty] | 5011 SLOCAN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| JUNG LANE | [24 empty] | 5031 CHAMBERS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KAMLOOPS STREET | [24 empty] | 5033 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KASLO STREET | [24 empty] | 505 W 62ND AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| KE KAIT PLACE | [24 empty] | 5055 EARLES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KEEFER PLACE | [24 empty] | 5077 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KEEFER STREET | [24 empty] | 508 HELMCKEN STREET |  |  |  | Yes | R90.1-2010 | FALSE
| KEITH DRIVE | [24 empty] | 5080 QUEBEC STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KELOWNA STREET | [24 empty] | 5085 MAIN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KEMPTON PLACE | [24 empty] | 5089 QUEBEC STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KERR STREET | [24 empty] | 510 SEYMOUR STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KERSLAND DRIVE | [24 empty] | 510 W GEORGIA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| KEVIN PLACE | [24 empty] | 5103 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KEYSTONE STREET | [24 empty] | 5105 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KIELDER COURT | [24 empty] | 5107 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KILLARNEY STREET | [24 empty] | 5115 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KILLDEER PLACE | [24 empty] | 5115 JOYCE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KINGHORNE MEWS | [24 empty] | 512 W 28TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| KINGS AVENUE | [24 empty] | 5120 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KINGS LYNN STREET | [24 empty] | 5151 OAK STREET |  |  |  | Yes | 90.1-2007 | FALSE
| KINGSWAY | [24 empty] | 5178 CHAMBERS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KINROSS STREET | [24 empty] | 5189 CLARENDON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KIRKLAND STREET | [24 empty] | 5190 CHAMBERS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KITCHENER STREET | [24 empty] | 520 E 1ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| KITSILANO DIVERSION | [24 empty] | 520 E KENT AVENUE SOUTH |  |  |  | Yes | 90.1-2007 | FALSE
| KNIGHT STREET | [24 empty] | 523 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| KOKANEE PLACE | [24 empty] | 525 ABBOTT STREET |  |  |  | Yes | 90.1-2007 | FALSE
| KOOTENAY STREET | [24 empty] | 5251 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| KULLAHUN DRIVE | [24 empty] | 528 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| LA SALLE STREET | [24 empty] | 531 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| LABURNUM STREET | [24 empty] | 531 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| LAGOON DRIVE | [24 empty] | 5325 WEST BOULEVARD |  |  |  | Yes | 90.1-2010 | FALSE
| LAHB AVENUE | [24 empty] | 535 SMITHE STREET |  |  |  | No | 90.1-2001 | FALSE
| LAKEWOOD DRIVE | [24 empty] | 535 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| LAKEWOOD STREET | [24 empty] | 538 W 7TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| LAMEY'S MILL ROAD | [24 empty] | 5411 HUDSON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LANARK STREET | [24 empty] | 5420 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LANCASTER PLACE | [24 empty] | 5428 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LANCASTER STREET | [24 empty] | 5444 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LANGARA AVENUE | [24 empty] | 5468 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LANGFORD AVENUE | [24 empty] | 547 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| LARCH STREET | [24 empty] | 5470 ORMIDALE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LATTA STREET | [24 empty] | 5474 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LAUREL STREET | [24 empty] | 549 E 16TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| LAURIER AVENUE | [24 empty] | 55 EXPO BOULEVARD |  |  |  | Yes | 90.1-2010 | FALSE
| LAVAL PLACE | [24 empty] | 550 TERMINAL AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| LE ROI STREET | [24 empty] | 550 W BROADWAY |  |  |  | Yes | 90.1-2007 | FALSE
| LEASIDE STREET | [24 empty] | 5500 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LEG-IN-BOOT SQUARE | [24 empty] | 5502 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LIARD PLACE | [24 empty] | 5515 BOUNDARY ROAD |  |  |  | Yes | 90.1-2007 | FALSE
| LIGHTHOUSE WAY | [24 empty] | 5516 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LILLOOET STREET | [24 empty] | 5538 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LILY STREET | [24 empty] | 555 SEYMOUR STREET |  |  |  | Yes | 90.1-2007 | FALSE
| LIME STREET | [24 empty] | 5555 DUNBAR STREET |  |  |  | Yes | 90.1-2007 | FALSE
| LIMEWOOD PLACE | [24 empty] | 558 E KENT AVENUE SOUTH |  |  |  | Yes | 90.1-2007 | FALSE
| LINCOLN STREET | [24 empty] | 5598 ORMIDALE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| LINDEN ROAD | [24 empty] | 563 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| LITTLE STREET | [24 empty] | 5648 VICTORIA DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| LOCARNO CRESCENT | [24 empty] | 565 GREAT NORTHERN WAY |  |  |  | Yes | 90.1-2010 | FALSE
| LOGAN STREET | [24 empty] | 5680 WILLOW STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LONG LIFE PLACE | [24 empty] | 5682 WILLOW STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LORD STREET | [24 empty] | 5687 BAILLIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LORNE STREET | [24 empty] | 5688 WILLOW STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LOUGHEED HIGHWAY | [24 empty] | 5689 BAILLIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LYNBROOK DRIVE | [24 empty] | 5699 BAILLIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| LYNMOOR PLACE | [24 empty] | 5711 RHODES STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MACDONALD STREET | [24 empty] | 580 MALKIN AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MACKENZIE PLACE | [24 empty] | 5805 WALES STREET |  |  |  | Yes | R90.1-2010 | FALSE
| MACKENZIE STREET | [24 empty] | 5809 WALES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MACKIE STREET | [24 empty] | 5821 WALES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MACLURE MEWS | [24 empty] | 5825 WALES STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MADDAMS STREET | [24 empty] | 5828 BLENHEIM STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MAGNOLIA STREET | [24 empty] | 5958 ST. GEORGE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MAIN STREET | [24 empty] | 601 E HASTINGS STREET |  |  |  | No | 90.1-2001 | FALSE
| MAINLAND STREET | [24 empty] | 601 W HASTINGS STREET |  |  |  | Yes | R90.1-2010 | FALSE
| MALI AVENUE | [24 empty] | 6070 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MALI LANE | [24 empty] | 6078 OAK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MALKIN AVENUE | [24 empty] | 6168 EAST BOULEVARD |  |  |  | Yes | 90.1-2010 | FALSE
| MALTA AVENUE | [24 empty] | 618 E KENT AVENUE SOUTH |  |  |  | Yes | 90.1-2007 | FALSE
| MALTA PLACE | [24 empty] | 620 CARDERO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MANITOBA STREET | [24 empty] | 6268 E Boulevard |  |  |  | Yes | 90.1-2010 | FALSE
| MANNERING AVENUE | [24 empty] | 6268 EAST BOULEVARD |  |  |  | Yes | 90.1-2007 | FALSE
| MANOR STREET | [24 empty] | 628 E KENT AVENUE SOUTH |  |  |  | Yes | 90.1-2007 | FALSE
| MANSON STREET | [24 empty] | 63 W 2ND AVENUE |  |  |  | No | 90.1-2001 | FALSE
| MAPLE CRESCENT | [24 empty] | 630 E BROADWAY |  |  |  | Yes | 90.1-2010 | FALSE
| MAPLE STREET | [24 empty] | 631 VICTORIA DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| MAQUINNA DRIVE | [24 empty] | 6311 CAMBIE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MARCHWOOD PLACE | [24 empty] | 633 MAIN STREET |  |  |  | Yes | R90.1-2010 | FALSE
| MARGUERITE STREET | [24 empty] | 633 W KING EDWARD AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MARINASIDE CRESCENT | [24 empty] | 6333 WEST BOULEVARD |  |  |  | Yes | 90.1-2010 | FALSE
| MARINE CRESCENT | [24 empty] | 6344 NANAIMO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MARINE WAY | [24 empty] | 6363 LANARK STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MARINER WALK | [24 empty] | 6383 CAMBIE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MARITIME MEWS | [24 empty] | 6391 FRASER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MARKET HILL | [24 empty] | 645 MALKIN AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MARLIN QUAY | [24 empty] | 650 EVANS AVENUE |  |  |  | No | 90.1-2001 | FALSE
| MARMION AVENUE | [24 empty] | 650 W 41ST AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| MARPOLE AVENUE | [24 empty] | 6508 KNIGHT STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MARQUETTE CRESCENT | [24 empty] | 655 W 41ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MARSHALL STREET | [24 empty] | 6555 VICTORIA DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| MARSTRAND AVENUE | [24 empty] | 66 W CORDOVA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MAST TOWER ROAD | [24 empty] | 662 KEEFER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MATAPAN CRESCENT | [24 empty] | 6665 MAIN STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MATHESON CRESCENT | [24 empty] | 6668 FRASER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MATTHEWS AVENUE | [24 empty] | 677 W 41ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MAXINE LANE | [24 empty] | 68 SMITHE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MAXWELL STREET | [24 empty] | 683 E 27TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MAYFAIR AVENUE | [24 empty] | 685 GREAT NORTHERN WAY |  |  |  | Yes | 90.1-2007 | FALSE
| MCBAIN AVENUE | [24 empty] | 688 E 18TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MCCLEERY STREET | [24 empty] | 688 E 19TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MCGEER STREET | [24 empty] | 688 TERMINAL AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MCGILL STREET | [24 empty] | 690 PIPELINE ROAD |  |  |  | Yes | 90.1-2010 | FALSE
| MCGUIGAN AVENUE | [24 empty] | 6933 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MCHARDY STREET | [24 empty] | 6939 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MCINTYRE DRIVE | [24 empty] | 6999 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MCKINNON STREET | [24 empty] | 7 E 6TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MCLEAN DRIVE | [24 empty] | 7 W 6TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MCMULLEN AVENUE | [24 empty] | 706 E 57TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MCNICOLL AVENUE | [24 empty] | 707 E 43RD AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MCRAE AVENUE | [24 empty] | 708 E 26TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MCSPADDEN AVENUE | [24 empty] | 709 E 39TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MEADOWLAND PLACE | [24 empty] | 709 SW MARINE DRIVE |  |  |  | Yes | 90.1-2007 | FALSE
| MEARES AVENUE | [24 empty] | 7128 ADERA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MELBOURNE STREET | [24 empty] | 7188 MACDONALD STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MELVILLE STREET | [24 empty] | 720 E HASTINGS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MENCHIONS MEWS | [24 empty] | 720 ROBSON STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MIDLOTHIAN AVENUE | [24 empty] | 7228 ADERA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MILLBANK | [24 empty] | 7238 CARRINGTON STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MILLER STREET | [24 empty] | 7249 CYPRESS STREET |  |  |  | Yes | R90.1-2010 | FALSE
| MILLSTONE STREET | [24 empty] | 727 E 17TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MILLYARD | [24 empty] | 7281 CYPRESS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MILROSS AVENUE | [24 empty] | 7281 FRASER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MILTON STREET | [24 empty] | 7295 CYPRESS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MINTO CRESCENT | [24 empty] | 7295 MAIN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MOBERLY ROAD | [24 empty] | 7298 ADERA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MOHAWK STREET | [24 empty] | 730 TERMINAL AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MONMOUTH AVENUE | [24 empty] | 7302 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MONS DRIVE | [24 empty] | 7303 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MONT ROYAL SQUARE | [24 empty] | 7319 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MONTCALM STREET | [24 empty] | 7325 CARNARVON STREET |  |  |  | No | 90.1-2001 | FALSE
| MONTGOMERY STREET | [24 empty] | 7325 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MORNINGSTAR CRESCENT | [24 empty] | 733 W 14TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| MORTON AVENUE | [24 empty] | 7342 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MOSCROP STREET | [24 empty] | 7350 FRASER STREET |  |  |  | Yes | R90.1-2010 | FALSE
| MOSS STREET | [24 empty] | 7358 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| MUIRFIELD DRIVE | [24 empty] | 738 E 29TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MUNROE CRESCENT | [24 empty] | 738 EVANS AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| MUSQUEAM AVENUE | [24 empty] | 7410 COLUMBIA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MUSQUEAM CLOSE | [24 empty] | 745 THURLOW STREET |  |  |  | Yes | 90.1-2007 | FALSE
| MUSQUEAM DRIVE | [24 empty] | 7450 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N BOUNDARY ROAD | [24 empty] | 7470 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N CASSIAR STREET | [24 empty] | 7480 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N COMMERCIAL DRIVE | [24 empty] | 7499 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N GARDEN DRIVE | [24 empty] | 75 W 1ST AVENUE |  |  |  | No | 90.1-2001 | FALSE
| N KAMLOOPS STREET | [24 empty] | 750 PACIFIC BOULEVARD |  |  |  | Yes | R90.1-2010 | FALSE
| N KASLO STREET | [24 empty] | 753 SEYMOUR STREET |  |  |  | Yes | R90.1-2010 | FALSE
| N KOOTENAY STREET | [24 empty] | 755 EVANS AVENUE |  |  |  | No | 90.1-2001 | FALSE
| N LAKEWOOD DRIVE | [24 empty] | 7601 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N NANAIMO STREET | [24 empty] | 7655 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N NOOTKA STREET | [24 empty] | 7657 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N PENTICTON STREET | [24 empty] | 774 W 14TH AVENUE |  |  |  | Yes | R90.1-2010 | FALSE
| N RENFREW STREET | [24 empty] | 777 RICHARDS STREET |  |  |  | Yes | R90.1-2010 | FALSE
| N RUPERT STREET | [24 empty] | 7790 CAMBIE STREET |  |  |  | Yes | R90.1-2010 | FALSE
| N SKEENA STREET | [24 empty] | 7800 VIVIAN DRIVE |  |  |  | Yes | 90.1-2010 | FALSE
| N SLOCAN STREET | [24 empty] | 7801 MANITOBA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N TEMPLETON DRIVE | [24 empty] | 7807 CAMBIE STREET |  |  |  | Yes | R90.1-2010+22% | FALSE
| N VICTORIA DRIVE | [24 empty] | 7828 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| N WINDERMERE STREET | [24 empty] | 7849 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NAIRN AVENUE | [24 empty] | 7904 MANITOBA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NANAIMO STREET | [24 empty] | 7906 MANITOBA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NANTON AVENUE | [24 empty] | 7920 MANITOBA STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NAPIER STREET | [24 empty] | 7928 YUKON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NAPLES WAY | [24 empty] | 7988 YUKON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NARVAEZ DRIVE | [24 empty] | 8 NANAIMO STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NASSAU DRIVE | [24 empty] | 8000 ROSS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NATAL STREET | [24 empty] | 803 W 12TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| NATIONAL AVENUE | [24 empty] | 8031 NUNAVUT LANE |  |  |  | Yes | 90.1-2007 | FALSE
| NAUTILUS CLOSE | [24 empty] | 8080 NUNAVUT LANE |  |  |  | Yes | 90.1-2010 | FALSE
| NEAL STREET | [24 empty] | 809 W 23RD AVENUE |  |  |  | Yes | R90.1-2010+22% | FALSE
| NELSON STREET | [24 empty] | 8101 SHAUGHNESSY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NEON STREET | [24 empty] | 8107 SHAUGHNESSY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NEW BRIGHTON ROAD | [24 empty] | 8111 SHAUGHNESSY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NEWCASTLE COURT | [24 empty] | 8131 NUNAVUT LANE |  |  |  | Yes | 90.1-2007 | FALSE
| NEWPORT AVENUE | [24 empty] | 8131 SHAUGHNESSY STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NICOLA STREET | [24 empty] | 8175 CAMBIE STREET |  |  |  | Yes | R90.1-2010 | FALSE
| NIGEL AVENUE | [24 empty] | 8188 LORD STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NOOTKA STREET | [24 empty] | 8189 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NORMANDY DRIVE | [24 empty] | 8199 CAMBIE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NORQUAY STREET | [24 empty] | 8223 Sherbrooke STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NORTH ARM AVENUE | [24 empty] | 8228 CROMPTON STREET |  |  |  | Yes | 90.1-2007 | FALSE
| NORTH FOOT OF MAIN STREET | [24 empty] | 8275 SHERBROOKE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NORTHERN STREET | [24 empty] | 8277 ONTARIO STREET |  |  |  | Yes | 90.1-2007 | FALSE
| NORTHUMBERLAND AVENUE | [24 empty] | 829 KEEFER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| NUNAVUT LANE | [24 empty] | 8324 GRANVILLE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| NW MARINE DRIVE | [24 empty] | 8385 FRASER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| OAK STREET | [24 empty] | 8475 FRASER STREET |  |  |  | Yes | 90.1-2007 | FALSE
| OBEN STREET | [24 empty] | 8488 CORNISH STREET |  |  |  | Yes | 90.1-2007 | FALSE
| ODLUM DRIVE | [24 empty] | 853 UNION STREET |  |  |  | Yes | 90.1-2010 | FALSE
| OGDEN AVENUE | [24 empty] | 8530 OSLER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| OLD BRIDGE COURT | [24 empty] | 8533 RIVER DISTRICT CROSSING |  |  |  | Yes | 90.1-2010 | FALSE
| OLD BRIDGE STREET | [24 empty] | 8538 RIVER DISTRICT CROSSING |  |  |  | Yes | 90.1-2010 | FALSE
| OLD BRIDGE WALK | [24 empty] | 8550 FRASER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| OLIVER CRESCENT | [24 empty] | 8555 GRANVILLE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| OLYMPIC STREET | [24 empty] | 8558 OSLER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ONTARIO PLACE | [24 empty] | 8572 OSLER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ONTARIO STREET | [24 empty] | 8578 OSLER STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ORIOLE WALK | [24 empty] | 8580 RIVER DISTRICT CROSSING |  |  |  | Yes | 90.1-2010 | FALSE
| ORMIDALE STREET | [24 empty] | 8585 YUKON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| ORTONA CRESCENT | [24 empty] | 8588 CORNISH STREET |  |  |  | Yes | 90.1-2007 | FALSE
| OSLER STREET | [24 empty] | 8588 JELLICOE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| OXFORD STREET | [24 empty] | 8601 MAIN STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PACIFIC BOULEVARD | [24 empty] | 8650 ASH STREET |  |  |  | No | 90.1-2001 | FALSE
| PACIFIC STREET | [24 empty] | 8675 BARNARD STREET |  |  |  | Yes | 90.1-2007 | FALSE
| PANDORA STREET | [24 empty] | 8683 KERR STREET |  |  |  | Yes | 90.1-2007 | FALSE
| PANTAGES LANE | [24 empty] | 8728 AISNE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PARK DRIVE | [24 empty] | 879 POWELL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PARKER STREET | [24 empty] | 88 W 1ST AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| PARKWAY DRIVE | [24 empty] | 880 W 28TH AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| PAT QUINN WAY | [24 empty] | 8811 LAUREL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PATON STREET | [24 empty] | 885 SALSBURY DRIVE |  |  |  | Yes | 90.1-2007 | FALSE
| PAULSON STREET | [24 empty] | 8855 LAUREL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PAYNE STREET | [24 empty] | 888 HOMER STREET |  |  |  | No | 90.1-2001 | FALSE
| PENDRELL STREET | [24 empty] | 8889 LAUREL STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PENNYFARTHING DRIVE | [24 empty] | 89 NELSON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PENTICTON STREET | [24 empty] | 89 W 2ND AVENUE |  |  |  | No | 90.1-2001 | FALSE
| PERROT MEWS | [24 empty] | 89 W GEORGIA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| PERRY STREET | [24 empty] | 901 E BROADWAY |  |  |  | Yes | 90.1-2010 | FALSE
| PETERSHAM AVENUE | [24 empty] | 9149 HUDSON STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PEVERIL AVENUE | [24 empty] | 932 E CORDOVA STREET |  |  |  | Yes | 90.1-2007 | FALSE
| PICTON STREET | [24 empty] | 933 E HASTINGS STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PIERVIEW CRESCENT | [24 empty] | 948 W 28TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| PINE CRESCENT | [24 empty] | 95 E 1ST AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| PINE STREET | [24 empty] | 95 W 15TH AVENUE |  |  |  | Yes | 90.1-2007 | FALSE
| PINEHURST DRIVE | [24 empty] | 950 GRANVILLE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| PINNACLE COURT | [24 empty] | 968 KINGSWAY |  |  |  | Yes | 90.1-2010 | FALSE
| PIPELINE ROAD | [24 empty] | 97 E 2ND AVENUE |  |  |  | Yes | 90.1-2010 | FALSE
| POINT GREY ROAD | [24 empty] | 970 UNION STREET |  |  |  | Yes | R90.1-2010 | FALSE
| POPLAR STREET | [24 empty] | 980 GEORGE STREET |  |  |  | Yes | 90.1-2010 | FALSE
| PORT AUTHORITY | [24 empty] | 980 HOWE STREET |  |  |  | Yes | R90.1-2010 | FALSE
| PORTER STREET | [24 empty] | 982 GRANVILLE STREET |  |  |  | Yes | 90.1-2007 | FALSE
| PORTSIDE COURT | [24 empty] | 988 W BROADWAY |  |  |  | Yes | 90.1-2010 | FALSE
| PORTSIDE DRIVE | [24 empty] | 999 SEYMOUR STREET |  |  |  | Yes | 90.1-2007 | FALSE
| POWELL STREET | [24 empty] | 999 W HASTINGS STREET |  |  |  | Yes | 90.1-2007 | FALSE
PRESCOTT STREET
PRESTON AVENUE
PRESTWICK DRIVE
PRICE STREET
PRINCE ALBERT STREET
PRINCE EDWARD STREET
PRINCESS AVENUE
PRIOR STREET
PROMENADE MEWS
PUGET DRIVE
PULLMAN PORTER STREET
QUADRA STREET
QUALICUM DRIVE
QUATSINO DRIVE
QUAYSIDE COURT
QUEBEC PLACE
QUEBEC STREET
QUEENS AVENUE
QUESNEL DRIVE
QUILCHENA CRESCENT
QUILCHENA PLACE
RADISSON STREET
RAE AVENUE
RAILSPUR ALLEY
RAILWAY STREET
RAINIER PLACE
RAINTREE COURT
RALEIGH STREET
RAND AVENUE
RAV GENERAL
RAVINE STREET
RAYMUR AVENUE
REBEKAH DRIVE
REDBUD LANE
REGIMENT SQUARE
REID STREET
RENFREW STREET
RHODES STREET
RICHARDS STREET
RICHELIEU AVENUE
RIEL PLACE
RINGWOOD AVENUE
RIVER DISTRICT CROSSING
RIVERGRASS DRIVE
RIVERWALK AVENUE
RIVERWOOD WAY
ROBSON STREET
ROCKPOOLE DRIVE
ROGERS STREET
ROLSTON STREET
ROSE STREET
ROSEBURY LANE
ROSEBURY WALK
ROSEDALE DRIVE
ROSEMARY BROWN LANE
ROSEMONT DRIVE
ROSS STREET
ROSSLAND STREET
ROUNDHOUSE MEWS
ROXBURGH CRESCENT
RUBY STREET
RUMBLE AVENUE
RUPERT STREET
SADDLE LANE
SAINT JOHN PAUL II WAY
SAINT JULIEN MEWS
SALAL DRIVE
SALERNO STREET
SALISH DRIVE
SALSBURY DRIVE
SALT STREET
SASAMAT PLACE
SASAMAT STREET
SASKATCHEWAN LANE
SAWCUT
SAWMILL CRESCENT
SAWYER'S LANE
SCALES PLACE
SCANTLINGS
SCARBORO AVENUE
SCHOOL AVENUE
SCHOOL GREEN
SCOTIA STREET
SE MARINE DRIVE
SEABREEZE WALK
SEAFORTH DRIVE
SEAGULL PLACE
SEE-EM-IA LANE
SELKIRK STREET
SEMANA CRESCENT
SEMLIN DRIVE
SENLAC STREET
SENNOK CRESCENT
SEYMOUR MEWS
SEYMOUR STREET
SHANGHAI ALLEY
SHAUGHNESSY STREET
SHAWNEE PLACE
SHERBROOKE STREET
SHOREPINE WALK
SIDNEY STREET
SIENUM PLACE
SI-LU DRIVE
SIMPSON AVENUE
SITKA SQUARE
SKANA DRIVE
SKEENA STREET
SKIPPER PLACE
SLOCAN STREET
SMITHE MEWS
SMITHE STREET
SOMERSET CRESCENT
SOMERVILLE STREET
SONGBIRD MEWS
SOPHIA STREET
SOTAO AVENUE
SOUTH SHORE CRESCENT
SOUTHERN STREET
SOUTHLANDS PLACE
SOUTHSIDE DRIVE
SPARBROOK CRESCENT
SPARROW PLACE
SPENCER STREET
SPINNAKER PLACE
SPRINGTREE DRIVE
SPRUCE STREET
SPYGLASS PLACE
ST. CATHERINES STREET
ST. CLAIR PLACE
ST. GEORGE STREET
ST. LAWRENCE STREET
ST. MARGARETS STREET
ST. REGIS LANE
STAINSBURY AVENUE
STAMFORD STREET
STAMP'S LANDING
STANLEY PARK DRIVE
STARBOARD SQUARE
STATION STREET
STAULO CRESCENT
STAUTLO AVENUE
STEPHENS STREET
STEWART STREET
STIKINE PLACE
STIRLING STREET
STOVOLD LANE
STRATHMORE MEWS
STRAUSS DRIVE
SUZHOU ALLEY
SW MARINE DRIVE
SWALLOW PLACE
SWANSACRE
SWITCHMEN STREET
TALISMAN AVENUE
TALON SQUARE
TAMARIND DRIVE
TAMATH CRESCENT
TANNER STREET
TANTALUS LANE
TAUNTON STREET
TAYLOR STREET
TEAKWOOD PLACE
TECUMSEH AVENUE
TED NORTHE LANE
TEMPLETON DRIVE
TERMINAL AVENUE
TERRA VITA PLACE
THE CASTINGS
THE CRESCENT
THELLAIWHALTUN AVENUE
THORNHILL DRIVE
THORNTON STREET
THREE CEDARS DRIVE
THRUSH PLACE
THURLOW STREET
TIDEWATER PLACE
TILNEY MEWS
TISDALL STREET
TOBA PLACE
TODD STREET
TODERICK STREET
TOLBOOTH
TOLMIE STREET
TOWNLEY STREET
TRAFALGAR STREET
TRIMBLE STREET
TRINITY STREET
TRIUMPH STREET
TROLLEY PLACE
TROUNCE ALLEY
TRUTCH STREET
TUAM PLACE
TUAQ DRIVE
TUGBOAT PLACE
TUPPER STREET
TURNBERRY CRESCENT
TURNER STREET
TYNE STREET
TYTAHUN CRESCENT
UNION STREET
UPLAND DRIVE
VALDEZ ROAD
VALIANT STREET
VALLEY DRIVE
VANNESS AVENUE
VENABLES STREET
VERNON DRIVE
VICTORIA DIVERSION
VICTORIA DRIVE
VIMY CRESCENT
VINE STREET
VIRTUAL WAY
VIVALDI PLACE
VIVIAN DRIVE
VIVIAN STREET
W 1ST AVENUE
W 2ND AVENUE
W 3RD AVENUE
W 4TH AVENUE
W 5TH AVENUE
W 6TH AVENUE
W 7TH AVENUE
W 8TH AVENUE
W 9TH AVENUE
W 10TH AVENUE
W 11TH AVENUE
W 12TH AVENUE
W 13TH AVENUE
W 14TH AVENUE
W 15TH AVENUE
W 16TH AVENUE
W 17TH AVENUE
W 18TH AVENUE
W 19TH AVENUE
W 20TH AVENUE
W 21ST AVENUE
W 22ND AVENUE
W 23RD AVENUE
W 24TH AVENUE
W 26TH AVENUE
W 27TH AVENUE
W 28TH AVENUE
W 29TH AVENUE
W 30TH AVENUE
W 31ST AVENUE
W 32ND AVENUE
W 33RD AVENUE
W 34TH AVENUE
W 35TH AVENUE
W 36TH AVENUE
W 37TH AVENUE
W 38TH AVENUE
W 39TH AVENUE
W 40TH AVENUE
W 41ST AVENUE
W 42ND AVENUE
W 43RD AVENUE
W 44TH AVENUE
W 45TH AVENUE
W 46TH AVENUE
W 47TH AVENUE
W 48TH AVENUE
W 49TH AVENUE
W 50TH AVENUE
W 51ST AVENUE
W 52ND AVENUE
W 53RD AVENUE
W 54TH AVENUE
W 55TH AVENUE
W 56TH AVENUE
W 57TH AVENUE
W 58TH AVENUE
W 59TH AVENUE
W 60TH AVENUE
W 61ST AVENUE
W 62ND AVENUE
W 63RD AVENUE
W 64TH AVENUE
W 65TH AVENUE
W 66TH AVENUE
W 67TH AVENUE
W 68TH AVENUE
W 69TH AVENUE
W 70TH AVENUE
W 71ST AVENUE
W 72ND AVENUE
W 73RD AVENUE
W 74TH AVENUE
W 75TH AVENUE
W 76TH AVENUE
W 77TH AVENUE
W BROADWAY
W CORDOVA STREET
W GEORGIA STREET
W HASTINGS STREET
W KENT AVENUE NORTH
W KENT AVENUE SOUTH
W KING EDWARD AVENUE
W PENDER STREET
W WATERFRONT ROAD
W WOODSTOCK AVENUE
WALDEN STREET
WALES STREET
WALKER STREET
WALL STREET
WALLACE CRESCENT
WALLACE PLACE
WALLACE STREET
WALNUT STREET
WALTER HARDWICK AVENUE
WANETA PLACE
WARD STREET
WATER STREET
WATERFORD DRIVE
WATERLEIGH DRIVE
WATERLOO STREET
WATERSIDE AVENUE
WATSON STREET
WAVERLEY AVENUE
WEAVER COURT
WEBBER AVENUE
WELLINGTON AVENUE
WELWYN STREET
WENONAH STREET
WERKS DRIVE
WESSEX STREET
WEST BOULEVARD
WEST POINT PLACE
WESTBANK PLACE
WESTBURY LANE
WESTBURY WALK
WESTERN STREET
WETHERSFIELD DRIVE
WEYMOOR PLACE
WHEELHOUSE SQUARE
WHITESPRAY DRIVE
WHITHORN COURT
WHITNEY PLACE
WHYTE AVENUE
WILLIAM STREET
WILLOW STREET
WILTSHIRE STREET
WINDERMERE STREET
WINDSOR STREET
WINLAW PLACE
WOLFE AVENUE
WOODLAND DRIVE
WORTHINGTON DRIVE
WORTHINGTON PLACE
WYLIE STREET
YALE STREET
YARDLEY AVENUE
YEW STREET
YEWBROOK PLACE
YORK AVENUE
YUCULTA CRESCENT
YUKON STREET
Note on B3: Insert the building's main address on this line. If your space is within the main building then also indicate the unit or suite number if any. For buildings with multiple commercial spaces, each having unique addresses, insert the building's main address here then the specific commercial space's address on the next row below.
Note on B4: If your space is a retail or commercial unit within a building, and your space has a different address from the main building, then put the building's address on the row above and the address of the retail or commercial unit on this row, starting with a unit number if any.
Note on C13: Most spaces have only one use. If more than one use then indicate all space uses. If more than one space or tenancy, then indicate uses, if more than one. Example: If a single tenancy (office) is becoming two tenancies (Retail, and Medical Office) then indicate based on size, with Primary being largest tenancy.
Note on C25: Do not include the City neighbourhood energy systems here. See below for declaration of City neighbourhood energy systems.
Note on D39: If building a complete wall or a complete roof, then comply with NECB 2015 envelope requirements and use envelope forms provided in the Building Envelpe tab. If only doing partial work or cladding work etc then submit only the Calculator to show that the envelope performance has not been made worse.
Note on D59: Indicate "X" if you are providing a water heating system that satisfies the requirements. Indicate "N/A" if a water heating system is not provided.
Note on E53: Insert source of input per these examples: - ASHRAE 62 - 2001 (except Addendum n) or - ASHRAE 62.1 - 20__ etc
Note on H3: Insert the suite or unit number if your space uses the address of the main building, otherwise leave blank.
Note on H4: Insert the suite number, if any, of your commercial space, otherwise leave blank.
Note on H13: Indicate Usage(s) starting with largest area, then add in order of decreasing area.
Note on H16: Use this cell to see a detailed description of the building(s) being considered above. To see the description, first choose the building from the drop box in this cell. The detailed description of the selected building will appear outside the checklist, to the right.
Note on I20: If not applicable, indicate "N/A". Indicate EUI requirement per the Rezoning Conditions.
Note on I21: If not applicable, indicate "N/A". Indicate EUI achieved per the modeling output (ECB).
Note on J28: If the existing building is already tied into an N/E system then choose the "Connected…" option. If within an N/E area but the building is not connected to the N/E system then choose the "Not Connected…" option. If the building is not within an N/E area then choose the "N/A" option.
Note on K3: Insert Building number.
Note on K4: Insert Tenancy number.
Note on N35: IMPORTANT: All Building Envelope work is automatically considered "Voluntary Upgrade". This can be indicated on row 12 above and on rows 76-78 below. Answer "Yes" if your scope of work on the building envelope includes the addition, deletion or replacement of glazing, skylights, doors, or insulation. If you are only refurbishing then reinstalling the original components then answer "No".
Note on N41: If you are adding lighting load, answer "Yes". If you are altering luminaires (replacing, removing, or relocating from one space into another) then answer "Yes", otherwise answer "No".
Note on N47: If you are adding any HVAC equipment (including kitchen exhaust and make-up air systems) that has an energy component such as motors ( >1 hp ), burners, coils, or heat exchangers, then answer "Yes". If you are only repairing existing equipment or moving diffuser locations then answer "No".
Note on N55: If you are adding any Service Water Heating equipment (boilers, hot water heater, on-demand system) that has an energy component such as motors, burners, coils, or heat exchangers, then answer "Yes". If you are only repairing or relocating existing equipment, then answer "No".
Note on N61: If you are adding or replacing Transformers, then answer "Yes", otherwise answer "No".
Note on O3: Insert building's street name by using drop box.
Note on O4: Insert tenancy's street name by using drop box.
Note on O13: Indicate area in square meters. Example: 3540 not 3540sqm.
Note on P35: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P41: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P47: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P55: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P61: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on Q20: Input to first decimal, without % sign. Example: 20.0 Indicate the required energy cost savings (reduction) beyond 90.1-2010, as stipulated by the Rezoning Conditions. Note: Savings to be measured in % energy cost saved.
Note on Q21: Input to first decimal, without % sign. Example: 20.0 This cell indicates the energy cost improvement (reduction) achieved beyond 90.1-2010, by percentage. Note, this measures energy cost savings, not energy savings.
Note on S37: Not required for Alteration projects (Part 11 TIs).
Note on S43: Not required for Alteration projects (Part 11 TIs).
Note on S49: Not required for Alteration projects (Part 11 TIs).
Note on S57: Not required for Alteration projects (Part 11 TIs).
Note on T21: New Construction or Core & Shell
Note on AB25: Indicate here any additional High Performance Energy system not listed within Drop-Down menu.
Note on AD24: Indicate here any additional Renewable Energy system not listed within Drop-Down menu.
Note on AE3: Submit without number, then update once permit number is known.
Note on AE20: Indicate level of LEED Certification required by Rezoning Conditions.
Note on AE21: Indicate level of LEED Certification achieved.
Note on AF13: Intent: Account for all conditioned non-Residential (commercial etc) spaces only. If area is zero or Not Applicable then input 0, not N/A or 0sqm. Space Area calculation: Calculate all areas except "non-conditioned" spaces. This means to exclude all outside spaces (patios), and include all interior spaces (ie storage, etc) as long as they are conditioned.
Note on AF14: If area is zero or Not Applicable then input 0, not N/A or 0 sqm. Intent: i) If scope includes Building Envelope work of a residential unit, use area of conditioned Residential space(s) only. ii) ASHRAE does not apply to areas within residential suites, just the common areas of residential buildings (and envelope per i above), therefore, indicate total area of common spaces being worked on. "Conditioned" Space Area calculation: Calculate all areas except "non-conditioned" spaces. This means to exclude all outside spaces (patios), and include all interior spaces (ie storage, etc) as long as they are conditioned.
Note on AF15: Intent: Account for all semiheated spaces only. If area is zero or Not Applicable then input 0, not N/A or 0sqm.
Note on AG16: Answer "Yes" if the entrance to the space is directly from the outdoors. Answer "No" if the entrance to the space is via another interior space such as a corridor or mall.
Note on AG17: Answer N/A if there is no outdoor entrance. Answer "Yes" if a new entrance is being built for the space, or if the existing outdoor entrance to the space is being modified. Answer "No" if the existing outdoor entrance to the space is not being modified.
Note on AG20: Indicate number of LEED energy pts (EAc1) required by Rezoning Conditions. If not specified, indicate N/A but still indicate number of pts achieved below.
Note on AG21: Indicate number of LEED energy pts (EAc1) achieved as shown on LEED Letter Template for EAc1.
Note on AG31: Are either architects or engineers involved in this project?
Note on AG33: Only Food and/or Beverage establishments are eligible for exterior patio heating systems.

## Building Envelope
Envelope Alterations for NECB/ZEBP Buildings
(See NECB/ZEBP alteration requirements)
Building Address: |  | 37 | 2203 | ABERDEEN STREET |  |  | Building Permit Application #:
Tenant Address:
Designer of Rec: |  |  |  |  | Email: |  | Telephone:
Contact Person: |  |  |  |  | Email: |  | Telephone:
Reconstructed and Altered Opaque Assemblies
Assembly # / Tag |  | Assembly Type | Assembly Name / Description | Type of Alteration |  | Assembly USImax Value (W/(m2∙K))
[6 empty] | Existing | Design | Code or Allowable (USI / U)
Added and Altered Fenestration Assemblies
Building's vertical fenestration (Door or Glazing);
i) Door/Glazing is being repaired/replaced/added?
ii) N/A
iii) N/A
iv) N/A
Building's horizontal fenestration;
i) Skylight is being repaired/replaced/added?
ii) N/A
Assembly # |  | Assembly Type | Assembly Name / Description | Type of Alteration |  | Assembly USImax Value (W/(m2∙K))
[6 empty] | Existing | Design | Code or Max Allowable (USI / U)
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [6 empty] | Version: 250403-1
Opaque Assemblies (Walls, Roof, Door, Slab, Floor)
|  | Yes/No |  | Type of Alt |  |  | VLOOKUP Table
|  | Yes |  | Repair |  |  | Wall | 0.290 / 0.051
|  | No |  | New (replace) |  |  | Roof | 0.164 / 0.029
|  |  |  | New (add) |  |  | Floor | 0.193 / 0.033
[7 empty] | Wall (w grnd) | 0.568 / 0.100
[7 empty] | Roof (w grnd) | 0.568 / 0.100
[7 empty] | Slab | 0.757 / 0.133
[7 empty] | Door | 2.12 / 0.373
Fenestration (Glazing, Door, Skylight)
|  | If glazing < 40% | [5 empty] | If replacement < 25% | If replacement > 25%
|  |  | Glazing | Repair |  | Glazing-Repair |  | Match existing, or better |  | Match existing, or better
|  |  | Glazing | New (replace) |  | Glazing-New (replace) |  | Match existing, or better |  | 1.9 / 0.335
|  |  | Glazing | New (add) |  | Glazing-New (add) |  | 1.9 / 0.335 |  | 1.9 / 0.335
|  |  | Door | Repair |  | Door-Repair |  | Match existing, or better |  | Match existing, or better
|  |  | Door | New (replace) |  | Door-New (replace) |  | Match existing, or better |  | 2.12 / 0.373
|  |  | Door | New (add) |  | Door-New (add) |  | 2.12 / 0.373 |  | 2.12 / 0.373
|  |  | Skylight | Repair |  | Skylight-Repair |  | Match existing, or better
|  |  | Skylight | New (replace) |  | Skylight-New (replace) |  | Match existing, or better
|  |  | Skylight | New (add) |  | Skylight-New (add) |  | 2.69 / 0.473
If glazing > 40%
[6 empty] | Glazing | Repair | Match existing, or better |  | Match existing, or better
[7 empty] | New (replace) | Match existing, or better |  | Match existing, or better
[7 empty] | New (add) | Trade-off |  | Trade-off
[6 empty] | Door | Repair | Match existing, or better |  | Match existing, or better
[7 empty] | New (replace) | Match existing, or better |  | Match existing, or better
[7 empty] | New (add) | Trade-off |  | Trade-off
|  | Skylight | [5 empty] | If skylight < 2% | If 2% > skylight < 5% |  | If skylight > 2%
|  |  | Skylight | Repair |  | Skylight-Repair |  | Match existing, or better |  | Match existing, or better | Match existing, or better
|  |  | Skylight | New (replace) |  | Skylight-New (replace) |  | Match existing, or better |  | 2.69 / 0.473 | 2.69 / 0.473
|  |  | Skylight | New (add) |  | Skylight-New (add) |  | 2.69 / 0.473 |  | 2.69 / 0.473 | Trade-off
Note on C37: Alteration rules per the NECB alteration language found within "Notes to Part 11" of the VBBL. See link.
Note on C41: Includes new skylights to be added.
Note on D43: Complete questions within Rows 33-41 before attempting to complete Fenestration Table below.
Note on F41: Ex: 1.7% to be indicated as 1.7
Note on I44: USI value for Repaired or replaced skylight assembly.
Note on J44: USI value for New or Repaired skylight assembly.

## Lighting
Lighting Alterations for NECB/ZEBP Buildings
(See NECB/ZEBP alteration requirements)
Building Address: |  | 37 | 2203 |  | ABERDEEN STREET |  |  |  |  | Building Permit Application #:
Tenant Address:
Designer of Rec: | [5 empty] | Email: |  |  |  | Telephone:
Contact Person: | [5 empty] | Email: |  |  |  | Telephone:
Interior Space |  |  |  |  | Lighting Power Alterations (W) |  |  |  | LPD (W/ft2) |  | Alteration Rules |  | Code Allowable LP | "Replaced" LP
ID # | Space Use (see Table 4.2.1.6.) |  |  | Area (ft2) | Existing | Added | Removed | Design (Final) | Design | Code | 50% Rule | Applicable
Controls
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
[8 empty] | 0 | [5 empty] | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | Version: 221222-1 | 0 | 0
Note on I10: Includes Replaced luminaires. Also, Removed LP cannot exceed Existing LP.
Note on J10: Total Lighting Power within each space per Articles 4.2.1.4. and 4.2.1.6..
Note on K47: Total Design LP divided by Total Area.
Note on L10: Adjusted to imperial W/sqft.
Note on L47: Total LP allowance divided by Total Area.
Note on M9: Alteration rules per the NECB alteration language found within "Notes to Part 11" of the VBBL. See link.
Note on M10: Exceptions 2.1.2.1.(a): For existing spaces already exceeding the Code LPD, Added LP cannot exceed 50% of Replaced LP. No limit to Added LP as long as Code LPD is not exceeded for that space.
Note on N10: Exception 2.1.2.1.(a): 2 kW LP replacement limit for alteration project to trigger only autoshutoff control requirement of 4.2.2.1.(20), otherwise all altered spaces must comply with entirety of Part 4.
Note on R9: The MIN of either Added or Removed.

## HVAC Equip
HVAC Alterations for NECB/ZEBP Buildings
(See NECB/ZEBP alteration requirements)
Building Address: | 37 | 2203 | ABERDEEN STREET |  |  |  | Building Permit Application #:
Tenant Address:
Designer of Rec: |  |  |  | Email: |  |  | Telephone:
Contact Person: |  |  |  | Email: |  |  | Telephone:
Equipment # | Equipment Description | Component or Equipment Type (Table 5.2.12.1.) | Cooling or Heating Capacity kW (Btuh) | Rating Condition |  | Equipment Performance (AFUE, CoP, EER, Et, SEER)
|  |  |  | kW | Condition | Design |  | Code (Table 5.2.12.1.)
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [6 empty] | Version: 221222-1

## Service Water Htg (new)
Service Water Heating Alterations for NECB/ZEBP Buildings
(See NECB/ZEBP alteration requirements)
Building Address: |  | 37 | 2203 |  | ABERDEEN STREET |  |  |  | Bldg Permit Applic #:
Tenant Address:
Designer of Rec: |  |  |  | Email: |  |  |  |  | Telephone:
Contact Person: |  |  |  | Email: |  |  |  |  | Telephone:
Equip # and Description |  | Component or Equipment Type (see Table 6.2.2.1.) | Q Rated Input (kW) | Vr Rated Capacity (L) |  | Vs Tank Volume (L) | Q / Vs (W/L) | FHR Rating Cond | Equipment Performance |  |  | Summation of All Numeric Formulas + Text Results |  |  |  |  | 2 | Applicant Inputs |  |  |  | 3 | 4 | 5 |  | 6 | 7 |  | 8 | 9 |  | 10 | 11 |  | 12 | 13 |  | 14 |  | 15 |  | 16 | 17 | 18 |  | 19 | 20 |  | 21
[9 empty] | Code |  | Design | [5 empty] | Formula | Q | Vr | Vs | FHR |  | SL (top inlet) |  | Equation Result | SL (bottom inlet) |  | Equation Result | SL (top inlet) |  | Equation Result | SL (bottom inlet) |  | Equation Result | SL (w division) |  | Equation Result | EF | Equation Result | Et (& instant) | Equation Result | Et and SL (w Q & SqRt Vr) combo |  |  | Equation Result | UEF (w FHR and Vs) |  | Equation Result
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[12 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [8 empty] | Version: 250411-1

## Data Line 4 Data Mine! (hidden)
No. | Data Extracted from (Tab Name) | Version | Building Address | Tenant or CRU no. | TIPs Eligible? | BOMA BESt? | b/t 90.1-2010? | BP Application No. | Primary Use | Primary Use Area | Secondary Use | Secondary Use Area | Tertiary Use | Tertiary Use Area | Non-Res Space Area | Resid Space Area | Semiheated Space Area | Exterior Heated Patio or Space Area | Any Reg Proff on Project? | Voluntry Upgrade, Repair, Small Suite, Minor Renov, Major Renov, Change MOC, Alteration (Addition) |  |  | N/E System | Base Bldg's N/E Status | TI's Thermal Energy Reqmt | Bldg Env | HVAC | SWH | Power | Lighting | Exemption | Categories of Alterations |  |  | Option Chosen (Required) | Non-Menu Item Chosen (Required)
| Data Mining Admin |  | General Building Information | [16 empty] | Permit Type(s) |  |  | N Energy Systems |  |  | ASHRAE - Scope of Work |  |  |  |  | Energy Upgrade
| Energy Checklist - Alterations | 230707-1 | ABERDEEN STREETABERDEEN STREET | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Note on U1: Zahra Teshnizi: http://evaluebc.bcassessment.ca/