## Intro, Info & Instructions
First TI projects within NECB&ZEBP Buildings - Energy Requirements
Applicability
This checklist is to be completed when performing "First" TI modifications to spaces never previously occupied. First TIs are therefore considered new construction. The application of NECB for new construction is limited to Major Occupancy A, B or F buildings or First TIs within buildings containing commercial D or E (Office, Retail), or buildings over 3 storeys containing multifamily dwellings.
STEP 1: Review the applicability of the energy process to your project
IMPORTANT Energy Checklist Process: Applicability
Some project types do not need to complete the energy checklist process. Projects where the entire scope of work is limited to that listed on the Energy Checklist Exemption form are exempt from the energy checklist and submission process.
How to apply for an exemption from the energy checklist process: Projects eligible for the energy checklist exemption can submit a completed Energy Checklist Exemption form found within the "Energy Requirements for Tenant Improvements" document (link below). Simply print out the exemption form and indicate the applicable project type(s). Include a hardcopy of the completed exemption form with your building permit application package.
IMPORTANT: Applying the Energy Checklist Exemption to an ineligible project will result in the building permit application being rejected on the basis of insufficient energy documentation.
Any project where the scope of work involves energy components of the building's systems, such as building envelope insulation, exterior doors or glazing/skylights, motors (>1 HP), burners, coils, heat exchangers, transformers, receptacles, lights, and/or controls for HVAC/Lighting/Service Water Heating systems, is required to complete the energy checklist and submission process.
Access the Energy Checklist Exemption form (within the Energy Requirements for Tenant Improvements document)
STEP 2: Review the Training Videos on how to use and apply the energy checklist and documentation
Tutorials: Training Videos
In January 2016, the City of Vancouver began providing web-based training videos to assist applicants with the energy checklists needed for building permit applications. These training videos are accessible via the following link:
Access the energy checklist Training Videos
STEP 3: Review the details for submission of energy documentation
Submission Format and Process
Effective September 15, 2025, this First TI checklist is to be submitted at the Building Permit application stage. Submit online with Building Permit application.
The content of this submission is to reflect the scope of work only, and not the base building equipment or envelope characteristics.
Occupancy Permit Application Stage
Complete the Occupancy Permit portion of the same energy checklist finalized during the building permit stage, then submit with your occupancy permit application.
Check the appropriate box that confirms whether or not the building permit stage energy checklist still accurately reflects the completed project. If not, then indicate this and resubmit the appropriate energy compliance forms needed to update the energy documents for this project. Resubmit only the forms needed to accurately reflect the changes made during the construction phase.
STEP 4: As needed, review detailed information to assist with the completion of the energy documentation
First Tenant Improvements
Use the this Checklist for "First TIs" when the following two conditions apply;
| i) | the project space has not been previously occupied, and
| ii) | the scope of work includes one or more of the following classifications: Repair, Minor Renovation, Major Renovation, Reconstruction, Additions, Changes of Major Occupancy Classification
Tenant improvements within a space not previously occupied are considered an extension of the original new construction and are to be treated like new construction.
Permit applications for "First TI" projects are to report their energy compliance for;
| i) | Part 10 of the Vancouver Building By-law (VBBL) and its reference of NECB 2020
Completing the Checklist for First TIs
Review the training videos - link provided above.
At the bottom of this screen there are a number of excel tabs. The next tab is the "NECB-ZEBP Checklist - First TI" and is to be completed and submitted for building permit. Note that there are several other tabs that show samples of various completed checklists. Be sure to follow these samples carefully to minimize the chance of delaying your permit application. It is important to note that checklists with blanks will be considered incomplete and the applicant will be asked to resubmit.
The checklist is divided into three parts;
|  | i) | General building information relevant to building energy performance,
|  | ii) | Energy requirements of the VBBL's Part 10 which references the ASHRAE and NECB energy standards/code, and
|  | iii) | Occupancy Permit stage
The content of this submission is to reflect the project's scope of work only, and not the base building equipment or envelope characteristics.
Specific information about how to apply and complete the energy sections can be found below.
General Building Data
Provide information about the building and project. Review the Samples (see tabs at bottom of screen) and complete the building and/or tenancy address information as per the samples.
Indicate the Use of the space or spaces, and their respective areas. Indicate the building's status with respect to Neighbourhood Energy (N/E) systems.
Space Use, Area & Performance Information
Most First TI projects are limited to a single space with a single space use such as office or retail, however some First TI projects involve a single space with multiple uses such as an office or retail in front with a workshop or warehouse or storage space or spaces in back. Some First TI projects will involve more than one space, sometimes on more than one floor. Indicate as many different space uses as is relevant to the project. Note that the "Building Use Description" tool is available if unsure about how to categorize a particular space and its use.
Indicate the area of each space listed in square meters. Also, indicate the total area of all spaces involved in the alteration project, when grouped as;
|  | - | "Non-residential Conditioned Space": | Spaces pertaining to Commercial, Retail, Industrial, Institutional uses etc.
|  | - | "Residential Conditioned Space": | Common areas in residential buildings including building envelope work of residential suites
|  | - | "Semiheated Space": | Spaces not fully "conditioned". Typically storage areas or work garages with overhead doors that are often opened or left open. Basically, not designed to maintain 22C.
(Note that the term "Conditioned" is meant to indicate "heated" and/or "air-conditioned" and suitable for continuous occupancy, as opposed to semiheated storage spaces not meant to be occupied.)
Building Entrance(s): Indicate if the space is accessed directly from the outdoors and whether or not the scope of work includes modifications to an existing outdoor entrance, or the creation of a new outdoor entrance.
Neighbourhood Energy (N/E) Systems
(Neighbourhood energy systems are energy supply systems such as the steam system in Gastown that supplies heat to buildings typically through below grade tie-in and heat exchanger systems)
First, if the building is within a N/E area then use the drop-down to indicate which system, otherwise indicate "N/A" if not within a N/E area. Next, indicate if the building is actually connected to the N/E system as some buildings are not connected. Answering these two questions will automatically result in the "TI's thermal energy requirement" being indicated in the last box. For instance, it may forbid the use of electric water heaters to be installed as the building may already provide stub-outs for heat exchanger type water heaters.
Energy Requirements: VBBL Part 10 & NECB 2020/ZEBP (10.2.2.5)
Part 10 of the VBBL references energy requirements in the form of standards (90.1/NECB/ZEBP) or individual requirements such as Articles 10.2.2.8. through 10.2.2.22.
10.2.2.19. is an allowance for limited exterior heating of patios for Food and Beverage establishments only. It has a number of requirements pertaining to type of heating and associated controls to prevent heating of unoccupied spaces and heating during warm weather conditions.
First Tis are treated as new construction and therefore NECB energy requirements apply accordingly, per the scope of work. The energy-related scope of work is determined through the following applicability process for the following areas;
Applying the NECB/ZEBP Energy Requirements for First TI Projects.
Frist TIs within buildings designed to NECB or ZEBP are required to use the NECB prescriptive approach, since, in the case of ZEBP (10.2.2.5) there are only modelling targets (TEUI/TEDI/GHGI) and no performance information for individual systems or components available. The following can be used to determine if NECB energy requirements apply based on the project's scope of work in these areas.
Building Envelope applies…
… if your scope of work on the building envelope includes the addition or deletion of glazing, skylights, doors, or insulation.
HVAC applies…
… if you are adding any HVAC equipment (including kitchen exhaust and make-up air systems) that has an energy component such as motors (greater than 1 HP), burners, coils, or heat exchangers.
Service Water Heating applies…
… if you are adding any Service Water Heating equipment (boilers, hot water heater, on-demand system) that has an energy component such as motors (greater than 1 HP), burners, coils, or heat exchangers.
Power applies…
… if you are adding new Transformers or new Receptacles.
Lighting applies…
… if you are adding lighting, and/or
… if you are replacing or removing lighting load to a space.
Steps:
| i) | Determine which sections apply and indicate on the checklist.
| ii) | Indicate the responsible party for each section.
| iii) | Complete each section accordingly.
Energy Statements on Drawings:
The Energy Statements on Drawings excel file can be accessed via the link provided on the Checklist. (Note: for smaller projects, this information can be written on the drawings by hand)
The purpose of this statement process is to provide a simple yet accurate way of determining the energy design criteria used in a building's original design, and subsequent upgrades. Energy statements on the drawings will provide a foundation upon which future design teams can assess building performance and determine the most effective approach to achieve their energy upgrade goals.
Effective January 1, 2015, the City of Vancouver's new Building By-law requires existing buildings to perform some form of energy upgrade/assessment when applying for building permits. Design teams will need historical energy design information in order to provide the best assessment for energy upgrades. Archive drawings with clear and concise energy design criteria will provide valuable assistance to future design teams.

## Validation Reference (hidden)
|  |  |  | Climate Zone |  |  | City | Zone
Yes |  |  |  | Zone 4 < 3000 HDD | 2 |  |  |  |  | Type of Building
No |  |  |  | Zone 5 3000 to 3999 HDD | 3 |  |  |  |  | New
N/A |  |  |  | Zone 6 4000 to 4999 HDD | 4 |  |  |  |  | Addition to existing building
|  |  |  | Zone 7A 5000 to 5999 HDD | 5
|  |  |  | Zone 7B 6000 to 6999 HDD | 6
|  |  |  | Zone 8 ≥ 7000 HDD | 7 |  |  |  |  | Building Area Method
Space-by-Space Method
Help Messages
Message 1 |  |  | Certain NECB requirements are climatic zone dependant. Please refer to Table C-1 for to find the number of heating degree-days (HDD) for your building location and enter the number of HDDs for your building location. If the building is semi-heated select the appropriate value from the 'Degree-Days Below 15C' column and enter the value under the "Heating Degree Days 15C" field.
Message 2 |  |  | A building with a design set-point temperature less that 15C is considered to be 'semi-heated'.
Message 3 |  |  | For additional information on calculating building envelope areas, please refer to Article 3.1.1.6.
5.2.12.1.-A | A | AA | Table 5.2.12.1.-A | Single-package, space-constrained | < 19 |  | Capacity < 19 kW | Single-package, space-constrained. Capacity < 19 kW | SEER = 13 HSPF V = 6.4 | SEER = HSPF V =
5.2.12.1.-B | B | BB |  | Single-package, others | < 19 |  | Capacity < 19 kW | Single-package, others. Capacity < 19 kW | SEER = 15 HSPF V = 7.4 | SEER = HSPF V =
5.2.12.1.-C | Cee | CC |  | Split system, space-constrained | < 19 |  | Capacity < 19 kW | Split system, space-constrained. Capacity < 19 kW | SEER = 13 HSPF V = 6.4 | SEER = HSPF V =
5.2.12.1.-D | D | DD |  | Split system, others | < 19 |  | Capacity < 19 kW | Split system, others. Capacity < 19 kW | SEER = 15 HSPF V = 7.4 | SEER = HSPF V =
5.2.12.1.-E | E | EE |  | Small-duct, high-velocity | < 19 |  | Capacity < 19 kW | Small-duct, high-velocity. Capacity < 19 kW | SEER = 13 HSPF V = 5.9 | SEER = HSPF V =
5.2.12.1.-F | F | FF |  | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode | ≥ 19 and < 40 | Electric resistance heating section or no heating section. | Capacity ≥ 19 and < 40 kW. RC: Electric resistance heating section or no heating section. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 19 and < 40 kW. RC: Electric resistance heating section or no heating section. | EER = 11.2 IEER = 12.9 | EER = IEER =
5.2.12.1.-G | G | GG |  |  | ≥ 19 and < 40 | Other types of heating sections. | Capacity ≥ 19 and < 40 kW. RC: Other types of heating sections. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 19 and < 40 kW. RC: Other types of heating sections. | EER = 11.0 IEER = 12.7 | EER = IEER =
5.2.12.1.-H | H | HH |  |  | ≥ 40 and < 70 | Electric resistance heating section or no heating section. | Capacity ≥ 40 and < 70 kW. RC: Electric resistance heating section or no heating section. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 40 and < 70 kW. RC: Electric resistance heating section or no heating section. | EER = 11.0 IEER = 12.4 | EER = IEER =
5.2.12.1.-I | I | II |  |  | ≥ 40 and < 70 | Other types of heating sections. | Capacity ≥ 40 and < 70 kW. RC: Other types of heating sections. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 40 and < 70 kW. RC: Other types of heating sections. | EER = 10.8 IEER = 12.2 | EER = IEER =
5.2.12.1.-J | J | JJ |  |  | ≥ 70 and < 223 | Electric resistance heating section or no heating section. | Capacity ≥ 70 and < 223 kW. RC: Electric resistance heating section or no heating section. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 70 and < 223 kW. RC: Electric resistance heating section or no heating section. | EER = 10.0 IEER = 11.6 | EER = IEER =
5.2.12.1.-K | K | KK |  |  | ≥ 70 and < 223 | Other types of heating sections. | Capacity ≥ 70 and < 223 kW. RC: Other types of heating sections. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 70 and < 223 kW. RC: Other types of heating sections. | EER = 9.8 IEER = 11.4 | EER = IEER =
5.2.12.1.-L | L | LL |  |  | ≥ 223 | Electric resistance heating section or no heating section. | Capacity ≥ 223 kW. RC: Electric resistance heating section or no heating section. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 223 kW. RC: Electric resistance heating section or no heating section. | EER = 9.7 IEER = 11.2 | EER = IEER =
5.2.12.1.-M | M | MM |  |  | ≥ 223 | Other types of heating sections. | Capacity ≥ 223 kW. RC: Other types of heating sections. | Large air conditioners and heat pumps, split and single-package, all electrical phases, in cooling mode. Capacity ≥ 223 kW. RC: Other types of heating sections. | EER = 9.5 IEER = 11.0 | EER = IEER =
5.2.12.1.-N | N | NN |  | Large heat pumps, split and single-package, all electrical phases, in heating mode | ≥ 19 and < 40 | at 8.3ºC | Capacity ≥ 19 and < 40 kW. RC: at 8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 19 and < 40 kW. RC: at 8.3ºC | COPh = 3.30 | COPh =
5.2.12.1.-O | O | OO |  |  | ≥ 19 and < 40 | at –8.3ºC | Capacity ≥ 19 and < 40 kW. RC: at –8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 19 and < 40 kW. RC: at –8.3ºC | COPh = 2.25 | COPh =
5.2.12.1.-P | P | PP |  |  | ≥ 40 and < 70 | at 8.3ºC | Capacity ≥ 40 and < 70 kW. RC: at 8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 40 and < 70 kW. RC: at 8.3ºC | COPh = 3.20 | COPh =
5.2.12.2. | Condensers | CCondensers |  |  | ≥ 40 and < 70 | at –8.3ºC | Capacity ≥ 40 and < 70 kW. RC: at –8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 40 and < 70 kW. RC: at –8.3ºC | COPh = 2.05 | COPh =
[5 empty] | ≥ 70 and < 223 | at 8.3ºC | Capacity ≥ 70 and < 223 kW. RC: at 8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 70 and < 223 kW. RC: at 8.3ºC | COPh = 3.20 | COPh =
[5 empty] | ≥ 70 and < 223 | at –8.3ºC | Capacity ≥ 70 and < 223 kW. RC: at –8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 70 and < 223 kW. RC: at –8.3ºC | COPh = 2.05 | COPh =
[5 empty] | ≥ 223 | at 8.3ºC | Capacity ≥ 223 kW. RC: at 8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 223 kW. RC: at 8.3ºC | COPh = 3.20 | COPh =
[5 empty] | ≥ 223 | at –8.3ºC | Capacity ≥ 223 kW. RC: at –8.3ºC | Large heat pumps, split and single-package, all electrical phases, in heating mode. Capacity ≥ 223 kW. RC: at –8.3ºC | COPh = 2.05 | COPh =
|  |  | Table 5.2.12.1.-B | SPVAC and SPVHP in cooling mode | < 70 | < 19 kW | Capacity < 70 kW. RC: < 19 kW | SPVAC and SPVHP in cooling mode. Capacity < 70 kW. RC: < 19 kW | EER = 11 | EER =
[5 empty] | < 70 | ≥ 19 kW and < 40 kW | Capacity < 70 kW. RC: ≥ 19 kW and < 40 kW | SPVAC and SPVHP in cooling mode. Capacity < 70 kW. RC: ≥ 19 kW and < 40 kW | EER = 10 | EER =
[5 empty] | < 70 | ≥ 40 kW and < 70 kW | Capacity < 70 kW. RC: ≥ 40 kW and < 70 kW | SPVAC and SPVHP in cooling mode. Capacity < 70 kW. RC: ≥ 40 kW and < 70 kW | EER = 10 | EER =
|  |  |  | SPVHP in heating mode | < 70 | < 19 kW | Capacity < 70 kW. RC: < 19 kW | SPVHP in heating mode. Capacity < 70 kW. RC: < 19 kW | COPh = 3.3 | COPh =
[5 empty] | < 70 | ≥ 19 kW and < 40 kW | Capacity < 70 kW. RC: ≥ 19 kW and < 40 kW | SPVHP in heating mode. Capacity < 70 kW. RC: ≥ 19 kW and < 40 kW | COPh = 3.0 | COPh =
[5 empty] | < 70 | ≥ 40 kW and < 70 kW | Capacity < 70 kW. RC: ≥ 40 kW and < 70 kW | SPVHP in heating mode. Capacity < 70 kW. RC: ≥ 40 kW and < 70 kW | COPh = 3.0 | COPh =
|  |  | Table 5.2.12.1.-C | Water-cooled and evaporatively cooled, split and single-package | < 19 | < 19 kW | Capacity < 19 kW. RC: < 19 kW | Water-cooled and evaporatively cooled, split and single-package. Capacity < 19 kW. RC: < 19 kW | EER = 12.1 IEER = 12.3 | EER = IEER =
|  |  |  | Water-cooled, split and single-package | ≥ 19 and < 40 | Electric resistance heating section or no heating section. | Capacity ≥ 19 and < 40 kW. RC: Electric resistance heating section or no heating section. | Water-cooled, split and single-package. Capacity ≥ 19 and < 40 kW. RC: Electric resistance heating section or no heating section. | EER = 12.1 IEER = 13.9 | EER = IEER =
[5 empty] | ≥ 19 and < 40 | Other types of heating sections. | Capacity ≥ 19 and < 40 kW. RC: Other types of heating sections. | Water-cooled, split and single-package. Capacity ≥ 19 and < 40 kW. RC: Other types of heating sections. | EER = 11.9 IEER = 13.7 | EER = IEER =
[5 empty] | ≥ 40 and < 70 | Electric resistance heating section or no heating section. | Capacity ≥ 40 and < 70 kW. RC: Electric resistance heating section or no heating section. | Water-cooled, split and single-package. Capacity ≥ 40 and < 70 kW. RC: Electric resistance heating section or no heating section. | EER = 12.5 IEER = 13.9 | EER = IEER =
[5 empty] | ≥ 40 and < 70 | Other types of heating sections. | Capacity ≥ 40 and < 70 kW. RC: Other types of heating sections. | Water-cooled, split and single-package. Capacity ≥ 40 and < 70 kW. RC: Other types of heating sections. | EER = 12.3 IEER = 13.7 | EER = IEER =
[5 empty] | ≥ 70 and < 223 | Electric resistance heating section or no heating section. | Capacity ≥ 70 and < 223 kW. RC: Electric resistance heating section or no heating section. | Water-cooled, split and single-package. Capacity ≥ 70 and < 223 kW. RC: Electric resistance heating section or no heating section. | EER = 12.4 IEER = 13.6 | EER = IEER =
[5 empty] | ≥ 70 and < 223 | Other types of heating sections. | Capacity ≥ 70 and < 223 kW. RC: Other types of heating sections. | Water-cooled, split and single-package. Capacity ≥ 70 and < 223 kW. RC: Other types of heating sections. | EER = 12.2 IEER = 13.4 | EER = IEER =
|  |  |  | Evaporatively cooled, split and single-package | ≥ 19 and < 40 | Electric resistance heating section or no heating section. | Capacity ≥ 19 and < 40 kW. RC: Electric resistance heating section or no heating section. | Evaporatively cooled, split and single-package. Capacity ≥ 19 and < 40 kW. RC: Electric resistance heating section or no heating section. | EER = 12.1 IEER = 12.3 | EER = IEER =
[5 empty] | ≥ 19 and < 40 | Other types of heating sections. | Capacity ≥ 19 and < 40 kW. RC: Other types of heating sections. | Evaporatively cooled, split and single-package. Capacity ≥ 19 and < 40 kW. RC: Other types of heating sections. | EER = 11.9 IEER = 12.1 | EER = IEER =
[5 empty] | ≥ 40 and < 70 | Electric resistance heating section or no heating section. | Capacity ≥ 40 and < 70 kW. RC: Electric resistance heating section or no heating section. | Evaporatively cooled, split and single-package. Capacity ≥ 40 and < 70 kW. RC: Electric resistance heating section or no heating section. | EER = 12.0 IEER = 12.2 | EER = IEER =
[5 empty] | ≥ 40 and < 70 | Other types of heating sections. | Capacity ≥ 40 and < 70 kW. RC: Other types of heating sections. | Evaporatively cooled, split and single-package. Capacity ≥ 40 and < 70 kW. RC: Other types of heating sections. | EER = 11.8 IEER = 12.0 | EER = IEER =
[5 empty] | ≥ 70 and < 223 | Electric resistance heating section or no heating section. | Capacity ≥ 70 and < 223 kW. RC: Electric resistance heating section or no heating section. | Evaporatively cooled, split and single-package. Capacity ≥ 70 and < 223 kW. RC: Electric resistance heating section or no heating section. | EER = 11.9 IEER = 12.1 | EER = IEER =
[5 empty] | ≥ 70 and < 223 | Other types of heating sections. | Capacity ≥ 70 and < 223 kW. RC: Other types of heating sections. | Evaporatively cooled, split and single-package. Capacity ≥ 70 and < 223 kW. RC: Other types of heating sections. | EER = 11.7 IEER = 11.9 | EER = IEER =
|  |  |  | Water-cooled, split and single-package | ≥ 223 | Electric resistance heating section or no heating section. | Capacity ≥ 223 kW. RC: Electric resistance heating section or no heating section. | Water-cooled, split and single-package. Capacity ≥ 223 kW. RC: Electric resistance heating section or no heating section. | EER = 12.2 IEER = 13.5 | EER = IEER =
[5 empty] | ≥ 223 | Other types of heating sections. | Capacity ≥ 223 kW. RC: Other types of heating sections. | Water-cooled, split and single-package. Capacity ≥ 223 kW. RC: Other types of heating sections. | EER = 12.0 IEER = 13.3 | EER = IEER =
|  |  |  | Evaporatively cooled, split and single-package | ≥ 223 | Electric resistance heating section or no heating section. | Capacity ≥ 223 kW. RC: Electric resistance heating section or no heating section. | Evaporatively cooled, split and single-package. Capacity ≥ 223 kW. RC: Electric resistance heating section or no heating section. | EER = 11.7 IEER = 11.9 | EER = IEER =
[5 empty] | ≥ 223 | Other types of heating sections. | Capacity ≥ 223 kW. RC: Other types of heating sections. | Evaporatively cooled, split and single-package. Capacity ≥ 223 kW. RC: Other types of heating sections. | EER = 11.5 IEER = 11.7 | EER = IEER =
|  |  | Table 5.2.12.1.-D | Air-cooled | ≥ 40 and < 70 |  | Capacity ≥ 40 and < 70 kW | Air-cooled. Capacity ≥ 40 and < 70 kW | EER = 11.2 | EER =
|  |  |  | Water-cooled and evaporatively cooled | ≥ 40 and < 70 |  | Capacity ≥ 40 and < 70 kW | Water-cooled and evaporatively cooled. Capacity ≥ 40 and < 70 kW | EER = 13.1 | EER =
|  |  |  | Air-cooled | ≥ 70 | ≥ 70 kW | Capacity ≥ 70 kW. RC: ≥ 70 kW | Air-cooled. Capacity ≥ 70 kW. RC: ≥ 70 kW | EER = 10.5 IEER = 11.8 | EER = IEER =
|  |  |  | Water-cooled and evaporatively cooled | ≥ 70 | ≥ 70 kW | Capacity ≥ 70 kW. RC: ≥ 70 kW | Water-cooled and evaporatively cooled. Capacity ≥ 70 kW. RC: ≥ 70 kW | EER = 13.5 IEER = 14.0 | EER = IEER =
|  |  | Table 5.2.12.1.-E | Water-to-air | < 5 | Water loop | Capacity < 5 kW. RC: Water loop | Water-to-air. Capacity < 5 kW. RC: Water loop | COPc = 3.58 COPh = 4.3 | COPc = COPh =
[5 empty] | ≥5 and< 40 | Water loop | Capacity ≥5 and< 40 kW. RC: Water loop | Water-to-air. Capacity ≥5 and< 40 kW. RC: Water loop | COPc = 3.81 COPh = 4.3 | COPc = COPh =
[5 empty] | < 40 | Groundwater | Capacity < 40 kW. RC: Groundwater | Water-to-air. Capacity < 40 kW. RC: Groundwater | COPc = 5.28 COPh = 3.7 | COPc = COPh =
[5 empty] | < 40 | Ground loop | Capacity < 40 kW. RC: Ground loop | Water-to-air. Capacity < 40 kW. RC: Ground loop | COPc = 4.13 COPh = 3.2 | COPc = COPh =
[5 empty] | < 40 | Water loop | Capacity < 40 kW. RC: Water loop | Water-to-air. Capacity < 40 kW. RC: Water loop | COPc = 3.11 COPh = 3.7 | COPc = COPh =
[5 empty] | < 40 | Groundwater | Capacity < 40 kW. RC: Groundwater | Water-to-air. Capacity < 40 kW. RC: Groundwater | COPc = 5.60 COPh = 3.4 | COPc = COPh =
[5 empty] | < 40 | Ground loop | Capacity < 40 kW. RC: Ground loop | Water-to-air. Capacity < 40 kW. RC: Ground loop | COPc = 4.21 COPh = 2.8 | COPc = COPh =
|  |  | Table 5.2.12.1.-F | Direct-expansion ground-source heat pumps | ≤ 21 |  | Capacity ≤ 21 kW | Direct-expansion ground-source heat pumps. Capacity ≤ 21 kW | COPc = 3.81 COPh = 3.1 | COPc = COPh =
[5 empty] | > 21 |  | Capacity > 21 kW | Direct-expansion ground-source heat pumps. Capacity > 21 kW | No reqm't
|  |  | Table 5.2.12.1.-G | PTAC and PTHP in cooling mode, standard and non-standard sizes | < 2.1 |  | Capacity < 2.1 kW | PTAC and PTHP in cooling mode, standard and non-standard sizes. Capacity < 2.1 kW | EER = 11.9 | EER =
[5 empty] | ≥ 2.1 and < 4.4 |  | Capacity ≥ 2.1 and < 4.4 kW | PTAC and PTHP in cooling mode, standard and non-standard sizes. Capacity ≥ 2.1 and < 4.4 kW | EER = 14.1 – (1.0435 × CapkW) | EER =
[5 empty] | ≥ 4.4 |  | Capacity ≥ 4.4 kW | PTAC and PTHP in cooling mode, standard and non-standard sizes. Capacity ≥ 4.4 kW | EER = 9.5 | EER =
|  |  |  | PTHP in heating mode, standard and non-standard sizes | < 2.1 |  | Capacity < 2.1 kW | PTHP in heating mode, standard and non-standard sizes. Capacity < 2.1 kW | COPh = 3.3 | COPh =
[5 empty] | ≥ 2.1 and < 4.4 |  | Capacity ≥ 2.1 and < 4.4 kW | PTHP in heating mode, standard and non-standard sizes. Capacity ≥ 2.1 and < 4.4 kW | COPh = 3.67 – (0.1739 × CapkW) | COPh =
[5 empty] | ≥ 4.4 |  | Capacity ≥ 4.4 kW | PTHP in heating mode, standard and non-standard sizes. Capacity ≥ 4.4 kW | COPh = 2.9 | COPh =
|  |  |  | Louvered, without reverse cycle | < 5.9 |  | Capacity < 5.9 kW | Louvered, without reverse cycle. Capacity < 5.9 kW | CEER = 10.7 | CEER =
[5 empty] | ≥ 5.9 and ≤ 10.6 |  | Capacity ≥ 5.9 and ≤ 10.6 kW | Louvered, without reverse cycle. Capacity ≥ 5.9 and ≤ 10.6 kW | CEER = 9.0 | CEER =
|  |  |  | Louvered, with reverse cycle | < 5.9 |  | Capacity < 5.9 kW | Louvered, with reverse cycle. Capacity < 5.9 kW | CEER = 9.8 | CEER =
[5 empty] | ≥ 5.9 and ≤ 10.6 |  | Capacity ≥ 5.9 and ≤ 10.6 kW | Louvered, with reverse cycle. Capacity ≥ 5.9 and ≤ 10.6 kW | CEER = 9.3 | CEER =
|  |  |  | Non-louvered, without reverse cycle | < 4.1 |  | Capacity < 4.1 kW | Non-louvered, without reverse cycle. Capacity < 4.1 kW | CEER = 9.6 | CEER =
[5 empty] | ≥ 4.1 and ≤ 10.6 |  | Capacity ≥ 4.1 and ≤ 10.6 kW | Non-louvered, without reverse cycle. Capacity ≥ 4.1 and ≤ 10.6 kW | CEER = 9.4 | CEER =
|  |  |  | Non-louvered, with reverse cycle | < 4.1 |  | Capacity < 4.1 kW | Non-louvered, with reverse cycle. Capacity < 4.1 kW | CEER = 9.3 | CEER =
[5 empty] | ≥ 4.1 and ≤ 10.6 |  | Capacity ≥ 4.1 and ≤ 10.6 kW | Non-louvered, with reverse cycle. Capacity ≥ 4.1 and ≤ 10.6 kW | CEER = 8.7 | CEER =
|  |  |  | Room air conditioners, casement only | All capacities |  | Capacity All capacities kW | Room air conditioners, casement only. Capacity All capacities kW | CEER = 9.5 | CEER =
|  |  |  | Room air conditioners, casement slider | All capacities |  | Capacity All capacities kW | Room air conditioners, casement only. Capacity All capacities kW | CEER = 10.4 | CEER =
|  |  | Table 5.2.12.1.-H | Air-cooled, floor-mounted, with or without fluid economizer | < 23 | Downflow or upflow, ducted | Capacity < 23 kW. RC: Downflow or upflow, ducted | Air-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Downflow or upflow, ducted | SCOP = 2.67 | SCOP =
[5 empty] | ≥ 23 and < 86 | Downflow or upflow, ducted | Capacity ≥ 23 and < 86 kW. RC: Downflow or upflow, ducted | Air-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 86 kW. RC: Downflow or upflow, ducted | SCOP = 2.55 | SCOP =
[5 empty] | ≥ 86 | Downflow or upflow, ducted | Capacity ≥ 86 kW. RC: Downflow or upflow, ducted | Air-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 86 kW. RC: Downflow or upflow, ducted | SCOP = 2.33 | SCOP =
[5 empty] | < 23 | Upflow, non-ducted | Capacity < 23 kW. RC: Upflow, non-ducted | Air-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Upflow, non-ducted | SCOP = 2.09 | SCOP =
[5 empty] | < 23 | Horizontal | Capacity < 23 kW. RC: Horizontal | Air-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Horizontal | SCOP = 2.65 | SCOP =
[5 empty] | ≥ 23 and < 70 | Upflow, non-ducted | Capacity ≥ 23 and < 70 kW. RC: Upflow, non-ducted | Air-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 70 kW. RC: Upflow, non-ducted | SCOP = 1.99 | SCOP =
[5 empty] | ≥ 23 and < 70 | Horizontal | Capacity ≥ 23 and < 70 kW. RC: Horizontal | Air-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 70 kW. RC: Horizontal | SCOP = 2.55 | SCOP =
[5 empty] | ≥ 70 | Upflow, non-ducted | Capacity ≥ 70 kW. RC: Upflow, non-ducted | Air-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 70 kW. RC: Upflow, non-ducted | SCOP = 1.81 | SCOP =
[5 empty] | ≥ 70 | Horizontal | Capacity ≥ 70 kW. RC: Horizontal | Air-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 70 kW. RC: Horizontal | SCOP = 2.47 | SCOP =
|  |  |  | Water-cooled, floor-mounted, with or without fluid economizer | < 23 | Downflow or upflow, ducted | Capacity < 23 kW. RC: Downflow or upflow, ducted | Water-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Downflow or upflow, ducted | SCOP = 2.74 | SCOP =
[5 empty] | ≥ 23 and < 86 | Downflow or upflow, ducted | Capacity ≥ 23 and < 86 kW. RC: Downflow or upflow, ducted | Water-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 86 kW. RC: Downflow or upflow, ducted | SCOP = 2.65 | SCOP =
[5 empty] | ≥ 86 | Downflow or upflow, ducted | Capacity ≥ 86 kW. RC: Downflow or upflow, ducted | Water-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 86 kW. RC: Downflow or upflow, ducted | SCOP = 2.61 | SCOP =
[5 empty] | < 23 | Upflow, non-ducted | Capacity < 23 kW. RC: Upflow, non-ducted | Water-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Upflow, non-ducted | SCOP = 2.44 | SCOP =
[5 empty] | < 23 | Horizontal | Capacity < 23 kW. RC: Horizontal | Water-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Horizontal | SCOP = 2.71 | SCOP =
[5 empty] | ≥ 23 and < 70 | Upflow, non-ducted | Capacity ≥ 23 and < 70 kW. RC: Upflow, non-ducted | Water-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 70 kW. RC: Upflow, non-ducted | SCOP = 2.34 | SCOP =
[5 empty] | ≥ 23 and < 70 | Horizontal | Capacity ≥ 23 and < 70 kW. RC: Horizontal | Water-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 70 kW. RC: Horizontal | SCOP = 2.60 | SCOP =
[5 empty] | ≥ 70 | Upflow, non-ducted | Capacity ≥ 70 kW. RC: Upflow, non-ducted | Water-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 70 kW. RC: Upflow, non-ducted | SCOP = 2.24 | SCOP =
[5 empty] | ≥ 70 | Horizontal | Capacity ≥ 70 kW. RC: Horizontal | Water-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 70 kW. RC: Horizontal | SCOP = 2.54 | SCOP =
|  |  |  | Glycol-cooled, floor-mounted, with or without fluid economizer | < 23 | Downflow or upflow, ducted | Capacity < 23 kW. RC: Downflow or upflow, ducted | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Downflow or upflow, ducted | SCOP = 2.48 | SCOP =
[5 empty] | ≥ 23 and < 86 | Downflow or upflow, ducted | Capacity ≥ 23 and < 86 kW. RC: Downflow or upflow, ducted | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 86 kW. RC: Downflow or upflow, ducted | SCOP = 2.16 | SCOP =
[5 empty] | ≥ 86 | Downflow or upflow, ducted | Capacity ≥ 86 kW. RC: Downflow or upflow, ducted | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 86 kW. RC: Downflow or upflow, ducted | SCOP = 2.12 | SCOP =
[5 empty] | < 23 | Upflow, non-ducted | Capacity < 23 kW. RC: Upflow, non-ducted | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Upflow, non-ducted | SCOP = 2.34 | SCOP =
[5 empty] | < 23 | Horizontal | Capacity < 23 kW. RC: Horizontal | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity < 23 kW. RC: Horizontal | SCOP = 2.44 | SCOP =
[5 empty] | ≥ 23 and < 70 | Upflow, non-ducted | Capacity ≥ 23 and < 70 kW. RC: Upflow, non-ducted | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 70 kW. RC: Upflow, non-ducted | SCOP = 1.99 | SCOP =
[5 empty] | ≥ 23 and < 70 | Horizontal | Capacity ≥ 23 and < 70 kW. RC: Horizontal | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 23 and < 70 kW. RC: Horizontal | SCOP = 2.10 | SCOP =
[5 empty] | ≥ 70 | Upflow, non-ducted | Capacity ≥ 70 kW. RC: Upflow, non-ducted | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 70 kW. RC: Upflow, non-ducted | SCOP = 1.94 | SCOP =
[5 empty] | ≥ 70 | Horizontal | Capacity ≥ 70 kW. RC: Horizontal | Glycol-cooled, floor-mounted, with or without fluid economizer. Capacity ≥ 70 kW. RC: Horizontal | SCOP = 2.10 | SCOP =
|  |  |  | Air-cooled, ceiling-mounted, free air discharge condenser, with or without fluid economizer | < 8.5 | Ducted | Capacity < 8.5 kW. RC: Ducted | Air-cooled, ceiling-mounted, free air discharge condenser, with or without fluid economizer. Capacity < 8.5 kW. RC: Ducted | SCOP = 2.01 | SCOP =
[5 empty] | < 8.5 | Non-ducted | Capacity < 8.5 kW. RC: Non-ducted | Air-cooled, ceiling-mounted, free air discharge condenser, with or without fluid economizer. Capacity < 8.5 kW. RC: Non-ducted | SCOP = 2.04 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Ducted | Capacity ≥ 8.5 and < 19 kW. RC: Ducted | Air-cooled, ceiling-mounted, free air discharge condenser, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Ducted | SCOP = 1.97 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Non-ducted | Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | Air-cooled, ceiling-mounted, free air discharge condenser, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | SCOP = 2.00 | SCOP =
[5 empty] | ≥ 19 | Ducted | Capacity ≥ 19 kW. RC: Ducted | Air-cooled, ceiling-mounted, free air discharge condenser, with or without fluid economizer. Capacity ≥ 19 kW. RC: Ducted | SCOP = 1.87 | SCOP =
[5 empty] | ≥ 19 | Non-ducted | Capacity ≥ 19 kW. RC: Non-ducted | Air-cooled, ceiling-mounted, free air discharge condenser, with or without fluid economizer. Capacity ≥ 19 kW. RC: Non-ducted | SCOP = 1.89 | SCOP =
|  |  |  | Air-cooled, ceiling-mounted, ducted condenser, with or without fluid economizer | < 8.5 | Ducted | Capacity < 8.5 kW. RC: Ducted | Air-cooled, ceiling-mounted, ducted condenser, with or without fluid economizer. Capacity < 8.5 kW. RC: Ducted | SCOP = 1.82 | SCOP =
[5 empty] | < 8.5 | Non-ducted | Capacity < 8.5 kW. RC: Non-ducted | Air-cooled, ceiling-mounted, ducted condenser, with or without fluid economizer. Capacity < 8.5 kW. RC: Non-ducted | SCOP = 1.68 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Ducted | Capacity ≥ 8.5 and < 19 kW. RC: Ducted | Air-cooled, ceiling-mounted, ducted condenser, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Ducted | SCOP = 1.78 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Non-ducted | Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | Air-cooled, ceiling-mounted, ducted condenser, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | SCOP = 1.81 | SCOP =
[5 empty] | ≥ 19 | Ducted | Capacity ≥ 19 kW. RC: Ducted | Air-cooled, ceiling-mounted, ducted condenser, with or without fluid economizer. Capacity ≥ 19 kW. RC: Ducted | SCOP = 1.68 | SCOP =
[5 empty] | ≥ 19 | Non-ducted | Capacity ≥ 19 kW. RC: Non-ducted | Air-cooled, ceiling-mounted, ducted condenser, with or without fluid economizer. Capacity ≥ 19 kW. RC: Non-ducted | SCOP = 1.70 | SCOP =
|  |  |  | Water-cooled, ceiling-mounted, with or without fluid economizer | < 8.5 | Ducted | Capacity < 8.5 kW. RC: Ducted | Water-cooled, ceiling-mounted, with or without fluid economizer. Capacity < 8.5 kW. RC: Ducted | SCOP = 2.33 | SCOP =
[5 empty] | < 8.5 | Non-ducted | Capacity < 8.5 kW. RC: Non-ducted | Water-cooled, ceiling-mounted, with or without fluid economizer. Capacity < 8.5 kW. RC: Non-ducted | SCOP = 2.36 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Ducted | Capacity ≥ 8.5 and < 19 kW. RC: Ducted | Water-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Ducted | SCOP = 2.23 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Non-ducted | Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | Water-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | SCOP = 2.26 | SCOP =
[5 empty] | ≥ 19 | Ducted | Capacity ≥ 19 kW. RC: Ducted | Water-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 19 kW. RC: Ducted | SCOP = 2.13 | SCOP =
[5 empty] | ≥ 19 | Non-ducted | Capacity ≥ 19 kW. RC: Non-ducted | Water-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 19 kW. RC: Non-ducted | SCOP = 2.16 | SCOP =
|  |  |  | Glycol-cooled, ceiling-mounted, with or without fluid economizer | < 8.5 | Ducted | Capacity < 8.5 kW. RC: Ducted | Glycol-cooled, ceiling-mounted, with or without fluid economizer. Capacity < 8.5 kW. RC: Ducted | SCOP = 1.92 | SCOP =
[5 empty] | < 8.5 | Non-ducted | Capacity < 8.5 kW. RC: Non-ducted | Glycol-cooled, ceiling-mounted, with or without fluid economizer. Capacity < 8.5 kW. RC: Non-ducted | SCOP = 1.95 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Ducted | Capacity ≥ 8.5 and < 19 kW. RC: Ducted | Glycol-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Ducted | SCOP = 1.88 | SCOP =
[5 empty] | ≥ 8.5 and < 19 | Non-ducted | Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | Glycol-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 8.5 and < 19 kW. RC: Non-ducted | SCOP = 1.93 | SCOP =
[5 empty] | ≥ 19 | Ducted | Capacity ≥ 19 kW. RC: Ducted | Glycol-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 19 kW. RC: Ducted | SCOP = 1.73 | SCOP =
[5 empty] | ≥ 19 | Non-ducted | Capacity ≥ 19 kW. RC: Non-ducted | Glycol-cooled, ceiling-mounted, with or without fluid economizer. Capacity ≥ 19 kW. RC: Non-ducted | SCOP = 1.76 | SCOP =
|  |  | Table 5.2.12.1.-I | Air-cooled air conditioners and heat pumps, with or without heat recovery | < 19 |  | Capacity < 19 kW | Air-cooled air conditioners and heat pumps, with or without heat recovery. Capacity < 19 kW | SEER = 15 HSPF V = 7.8 | SEER = HSPF V =
|  |  |  | Air-cooled air conditioners | ≥ 19 and < 40 |  | Capacity ≥ 19 and < 40 kW | Air-cooled air conditioners. Capacity ≥ 19 and < 40 kW | EER = 11.2 IEER = 15.5 | EER = IEER =
[5 empty] | ≥ 40 and < 70 |  | Capacity ≥ 40 and < 70 kW | Air-cooled air conditioners. Capacity ≥ 40 and < 70 kW | EER = 11.0 IEER = 14.9 | EER = IEER =
[5 empty] | ≥ 70 |  | Capacity ≥ 70 kW | Air-cooled air conditioners. Capacity ≥ 70 kW | EER = 10.0 IEER = 13.9 | EER = IEER =
|  |  |  | Air-source heat pumps, with or without heat recovery | ≥ 19 and < 40 | COPh evaluated at 8.3ºC db / 6.1ºC wb, and at –8.3ºC db / –9.4ºC wb | Capacity ≥ 19 and < 40 kW. RC: COPh evaluated at 8.3ºC db / 6.1ºC wb, and at –8.3ºC db / –9.4ºC wb | Air-source heat pumps, with or without heat recovery. Capacity ≥ 19 and < 40 kW. RC: COPh evaluated at 8.3ºC db / 6.1ºC wb, and at –8.3ºC db / –9.4ºC wb | EER = 10.8 IEER = 14.4 COPh = 3.30 COPh = 2.25 | EER = IEER = COPh = COPh =
[5 empty] | ≥ 40 and < 70 | COPh evaluated at 8.3ºC db / 6.1ºC wb, and –8.3ºC db / –9.4ºC wb | Capacity ≥ 40 and < 70 kW. RC: COPh evaluated at 8.3ºC db / 6.1ºC wb, and –8.3ºC db / –9.4ºC wb | Air-source heat pumps, with or without heat recovery. Capacity ≥ 40 and < 70 kW. RC: COPh evaluated at 8.3ºC db / 6.1ºC wb, and –8.3ºC db / –9.4ºC wb | EER = 10.4 IEER = 13.7 COPh = 3.20 COPh = 2.05 | EER = IEER = COPh = COPh =
[5 empty] | ≥ 70 | COPh = evaluated at 8.3ºC db / 6.1ºC wb, and at –8.3ºC db / –9.4ºC wb | Capacity ≥ 70 kW. RC: COPh = evaluated at 8.3ºC db / 6.1ºC wb, and at –8.3ºC db / –9.4ºC wb | Air-source heat pumps, with or without heat recovery. Capacity ≥ 70 kW. RC: COPh = evaluated at 8.3ºC db / 6.1ºC wb, and at –8.3ºC db / –9.4ºC wb | EER = 9.3 IEER = 12.5 COPh = 3.20 COPh = 2.05 | EER = IEER = COPh = COPh =
|  |  |  | Water-source heat pumps, with or without heat recovery | < 40 |  | Capacity < 40 kW | Water-source heat pumps, with or without heat recovery. Capacity < 40 kW | EER = 11.8 IEER = 15.8 COPh = 4.3 | EER = IEER = COPh =
[5 empty] | ≥ 40 |  | Capacity ≥ 40 kW | Water-source heat pumps, with or without heat recovery. Capacity ≥ 40 kW | EER = 9.8 IEER = 12.0 COPh = 4.0 | EER = IEER = COPh =
|  |  |  | Groundwater source heat pumps, with or without heat recovery | < 40 |  | Capacity < 40 kW | Groundwater source heat pumps, with or without heat recovery. Capacity < 40 kW | EER = 16.2 COPh = 3.6 | EER = COPh =
[5 empty] | ≥ 40 |  | Capacity ≥ 40 kW | Groundwater source heat pumps, with or without heat recovery. Capacity ≥ 40 kW | EER = 13.8 COPh = 3.3 | EER = COPh =
|  |  |  | Ground-source heat pumps, with or without heat recovery | < 40 |  | Capacity < 40 kW | Ground-source heat pumps, with or without heat recovery. Capacity < 40 kW | EER = 13.2 COPh = 3.1 | EER = COPh =
[5 empty] | ≥ 40 |  | Capacity ≥ 40 kW | Ground-source heat pumps, with or without heat recovery. Capacity ≥ 40 kW | EER = 10.8 COPh = 2.8 | EER = COPh =
|  |  | Table 5.2.12.1.-J | Air-cooled | > 0 |  | Capacity > 0 kW | Air-cooled. Capacity > 0 kW | ISMRE = 1.8 | ISMRE =
|  |  |  | Air-source heat pumps | > 0 |  | Capacity > 0 kW | Air-source heat pumps. Capacity > 0 kW | ISMRE = 1.8 ISCOP = 1.2 | ISMRE = ISCOP =
|  |  |  | Water-cooled | > 0 | Cooling tower / condenser water | Capacity > 0 kW. RC: Cooling tower / condenser water | Water-cooled. Capacity > 0 kW. RC: Cooling tower / condenser water | ISMRE = 2.2 | ISMRE =
[5 empty] | > 0 | Chilled water | Capacity > 0 kW. RC: Chilled water | Water-cooled. Capacity > 0 kW. RC: Chilled water | ISMRE = 2.7 | ISMRE =
|  |  |  | Water-source heat pumps | > 0 | Water source | Capacity > 0 kW. RC: Water source | Water-source heat pumps. Capacity > 0 kW. RC: Water source | ISMRE = 1.8 ISCOP = 3.5 | ISMRE = ISCOP =
[5 empty] | > 0 | Groundwater source | Capacity > 0 kW. RC: Groundwater source | Water-source heat pumps. Capacity > 0 kW. RC: Groundwater source | ISMRE = 2.3 ISCOP = 3.2 | ISMRE = ISCOP =
[5 empty] | > 0 | Ground-source, closed loop | Capacity > 0 kW. RC: Ground-source, closed loop | Water-source heat pumps. Capacity > 0 kW. RC: Ground-source, closed loop | ISMRE = 2.2 ISCOP = 2.0 | ISMRE = ISCOP =
|  |  |  | Air-cooled, with energy recovery | > 0 |  | Capacity > 0 kW | Air-cooled, with energy recovery. Capacity > 0 kW | ISMRE = 2.4 | ISMRE =
|  |  |  | Air-source heat pumps, with energy recovery | > 0 |  | Capacity > 0 kW | Air-source heat pumps, with energy recovery. Capacity > 0 kW | ISMRE = 2.4 ISCOP = 3.3 | ISMRE = ISCOP =
|  |  |  | Water-cooled, with energy recovery | > 0 | Cooling tower / condenser water | Capacity > 0 kW. RC: Cooling tower / condenser water | Water-cooled, with energy recovery. Capacity > 0 kW. RC: Cooling tower / condenser water | ISMRE = 2.4 | ISMRE =
[5 empty] | > 0 | Chilled water | Capacity > 0 kW. RC: Chilled water | Water-cooled, with energy recovery. Capacity > 0 kW. RC: Chilled water | ISMRE = 3.0 | ISMRE =
|  |  |  | Water-source heat pumps, with energy recovery | > 0 | Water source | Capacity > 0 kW. RC: Water source | Water-source heat pumps, with energy recovery. Capacity > 0 kW. RC: Water source | ISMRE = 2.2 ISCOP = 4.8 | ISMRE = ISCOP =
[5 empty] | > 0 | Groundwater source | Capacity > 0 kW. RC: Groundwater source | Water-source heat pumps, with energy recovery. Capacity > 0 kW. RC: Groundwater source | ISMRE = 2.6 ISCOP = 4.0 | ISMRE = ISCOP =
[5 empty] | > 0 | Ground-source, closed loop | Capacity > 0 kW. RC: Ground-source, closed loop | Water-source heat pumps, with energy recovery. Capacity > 0 kW. RC: Ground-source, closed loop | ISMRE = 2.4 ISCOP = 3.8 | ISMRE = ISCOP =
|  |  | Table 5.2.12.1.-K | Air-cooled, with or without remote condensers, all types of compressors | < 528 | Path A (typ full load operation) | Path A (typ full load operation), Capacity < 528 kW | Air-cooled, with or without remote condensers, all types of compressors. Path A (typ full load operation), Capacity < 528 kW | COPc = 2.985 IPLV = 4.048 | COPc = IPLV =
[5 empty] | ≥ 528 |  | Path A (typ full load operation), Capacity ≥ 528 kW | Air-cooled, with or without remote condensers, all types of compressors. Path A (typ full load operation), Capacity ≥ 528 kW | COPc = 2.985 IPLV = 4.137 | COPc = IPLV =
|  |  |  | Water-cooled, rotary screw, scroll, or reciprocating compressor | < 264 |  | Path A (typ full load operation), Capacity < 264 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path A (typ full load operation), Capacity < 264 kW | COPc = 4.694 IPLV = 5.867 | COPc = IPLV =
[5 empty] | ≥ 264 and < 528 |  | Path A (typ full load operation), Capacity ≥ 264 and < 528 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path A (typ full load operation), Capacity ≥ 264 and < 528 kW | COPc = 4.889 IPLV = 6.286 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 5.334 IPLV = 6.519 | COPc = IPLV =
[5 empty] | ≥ 1 055 and < 2 110 |  | Path A (typ full load operation), Capacity ≥ 1 055 and < 2 110 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path A (typ full load operation), Capacity ≥ 1 055 and < 2 110 kW | COPc = 5.771 IPLV = 6.770 | COPc = IPLV =
[5 empty] | ≥ 2 110 |  | Path A (typ full load operation), Capacity ≥ 2 110 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path A (typ full load operation), Capacity ≥ 2 110 kW | COPc = 6.286 IPLV = 7.041 | COPc = IPLV =
|  |  |  | Water-cooled, centrifugal compressor | < 528 |  | Path A (typ full load operation), Capacity < 528 kW | Water-cooled, centrifugal compressor. Path A (typ full load operation), Capacity < 528 kW | COPc = 5.771 IPLV = 6.401 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | Water-cooled, centrifugal compressor. Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 5.771 IPLV = 6.401 | COPc = IPLV =
[5 empty] | ≥ 1 055 and < 1 407 |  | Path A (typ full load operation), Capacity ≥ 1 055 and < 1 407 kW | Water-cooled, centrifugal compressor. Path A (typ full load operation), Capacity ≥ 1 055 and < 1 407 kW | COPc = 6.286 IPLV = 6.770 | COPc = IPLV =
[5 empty] | ≥ 1 407 |  | Path A (typ full load operation), Capacity ≥ 1 407 kW | Water-cooled, centrifugal compressor. Path A (typ full load operation), Capacity ≥ 1 407 kW | COPc = 6.286 IPLV = 7.041 | COPc = IPLV =
|  |  |  | Air-cooled, with or without remote condensers, all types of compressors | < 528 | Path B (typ part load operation) | Path B (typ part load operation), Capacity < 528 kW | Air-cooled, with or without remote condensers, all types of compressors. Path B (typ part load operation), Capacity < 528 kW | COPc = 2.866 IPLV = 4.669 | COPc = IPLV =
[5 empty] | ≥ 528 |  | Path B (typ part load operation), Capacity ≥ 528 kW | Air-cooled, with or without remote condensers, all types of compressors. Path B (typ part load operation), Capacity ≥ 528 kW | COPc = 2.866 IPLV = 4.758 | COPc = IPLV =
|  |  |  | Water-cooled, rotary screw, scroll, or reciprocating compressor | < 264 |  | Path B (typ part load operation), Capacity < 264 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path B (typ part load operation), Capacity < 264 kW | COPc = 4.513 IPLV = 7.041 | COPc = IPLV =
[5 empty] | ≥ 264 and < 528 |  | Path B (typ part load operation), Capacity ≥ 264 and < 528 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path B (typ part load operation), Capacity ≥ 264 and < 528 kW | COPc = 4.694 IPLV = 7.184 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 5.177 IPLV = 8.001 | COPc = IPLV =
[5 empty] | ≥ 1 055 and < 2 110 |  | Path B (typ part load operation), Capacity ≥ 1 055 and < 2 110 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path B (typ part load operation), Capacity ≥ 1 055 and < 2 110 kW | COPc = 5.633 IPLV = 8.586 | COPc = IPLV =
[5 empty] | ≥ 2 110 |  | Path B (typ part load operation), Capacity ≥ 2 110 kW | Water-cooled, rotary screw, scroll, or reciprocating compressor. Path B (typ part load operation), Capacity ≥ 2 110 kW | COPc = 6.018 IPLV = 9.264 | COPc = IPLV =
|  |  |  | Water-cooled, centrifugal compressor | < 528 |  | Path B (typ part load operation), Capacity < 528 kW | Water-cooled, centrifugal compressor. Path B (typ part load operation), Capacity < 528 kW | COPc = 5.065 IPLV = 8.001 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | Water-cooled, centrifugal compressor. Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 5.544 IPLV = 8.801 | COPc = IPLV =
[5 empty] | ≥ 1 055 and < 1 407 |  | Path B (typ part load operation), Capacity ≥ 1 055 and < 1 407 kW | Water-cooled, centrifugal compressor. Path B (typ part load operation), Capacity ≥ 1 055 and < 1 407 kW | COPc = 5.917 IPLV = 9.027 | COPc = IPLV =
[5 empty] | ≥ 1 407 |  | Path B (typ part load operation), Capacity ≥ 1 407 kW | Water-cooled, centrifugal compressor. Path B (typ part load operation), Capacity ≥ 1 407 kW | COPc = 6.018 IPLV = 9.264 | COPc = IPLV =
|  |  |  | Single-effect absorption, air-cooled | > 0 |  | Capacity > 0 kW | Single-effect absorption, air-cooled. Capacity > 0 kW | COPc = 0.600 | COPc =
|  |  |  | Single-effect absorption, water-cooled | > 0 |  | Capacity > 0 kW | Single-effect absorption, water-cooled. Capacity > 0 kW | COPc = 0.700 | COPc =
|  |  |  | Double-effect absorption, indirect fire | > 0 |  | Capacity > 0 kW | Double-effect absorption, indirect fire. Capacity > 0 kW | COPc = 1.000 IPLV = 1.050 | COPc = IPLV =
|  |  |  | Double-effect absorption, direct fire | > 0 |  | Capacity > 0 kW | Double-effect absorption, direct fire. Capacity > 0 kW | COPc = 1.000 IPLV = 1.000 | COPc = IPLV =
|  |  | Table 5.2.12.1.-L | Air-source heat pumps, in cooling mode | < 528 | Path A (typ full load operation) | Path A (typ full load operation), Capacity < 528 kW | Air-source heat pumps, in cooling mode. Path A (typ full load operation), Capacity < 528 kW | COPc = 2.836 IPLV = 3.846 | COPc = IPLV =
[5 empty] | ≥ 528 |  | Path A (typ full load operation), Capacity ≥ 528 kW | Air-source heat pumps, in cooling mode. Path A (typ full load operation), Capacity ≥ 528 kW | COPc = 2.836 IPLV = 3.930 | COPc = IPLV =
|  |  |  | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode | < 264 |  | Path A (typ full load operation), Capacity < 264 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path A (typ full load operation), Capacity < 264 kW | COPc = 4.659 IPLV = 5.574 | COPc = IPLV =
[5 empty] | ≥ 264 and < 528 |  | Path A (typ full load operation), Capacity ≥ 264 and < 528 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path A (typ full load operation), Capacity ≥ 264 and < 528 kW | COPc = 4.645 IPLV = 5.972 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 5.067 IPLV = 6.193 | COPc = IPLV =
[5 empty] | ≥ 1 055 and < 2 110 |  | Path A (typ full load operation), Capacity ≥ 1 055 and < 2 110 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path A (typ full load operation), Capacity ≥ 1 055 and < 2 110 kW | COPc = 5.482 IPLV = 6.432 | COPc = IPLV =
[5 empty] | ≥ 2 110 |  | Path A (typ full load operation), Capacity ≥ 2 110 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path A (typ full load operation), Capacity ≥ 2 110 kW | COPc = 5.072 IPLV = 6.689 | COPc = IPLV =
|  |  |  | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode | < 264 |  | Path A (typ full load operation), Capacity < 264 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path A (typ full load operation), Capacity < 264 kW | COPc = 5.482 IPLV = 6.081 | COPc = IPLV =
[5 empty] | ≥ 264 and < 528 |  | Path A (typ full load operation), Capacity ≥ 264 and < 528 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path A (typ full load operation), Capacity ≥ 264 and < 528 kW | COPc = 5.482 IPLV = 6.081 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path A (typ full load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 5.972 IPLV = 6.432 | COPc = IPLV =
[5 empty] | ≥ 1 055 |  | Path A (typ full load operation), Capacity ≥ 1 055 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path A (typ full load operation), Capacity ≥ 1 055 kW | COPc = 5.972 IPLV = 6.689 | COPc = IPLV =
|  |  |  | Air-source heat pumps, in cooling mode | < 528 | Path B (typ part load operation) | Path B (typ part load operation), Capacity < 528 kW | Air-source heat pumps, in cooling mode. Path B (typ part load operation), Capacity < 528 kW | COPc = 2.723 IPLV = 4.436 | COPc = IPLV =
[5 empty] | ≥ 528 |  | Path B (typ part load operation), Capacity ≥ 528 kW | Air-source heat pumps, in cooling mode. Path B (typ part load operation), Capacity ≥ 528 kW | COPc = 2.723 IPLV = 4.520 | COPc = IPLV =
|  |  |  | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode | < 264 |  | Path B (typ part load operation), Capacity < 264 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path B (typ part load operation), Capacity < 264 kW | COPc = 4.287 IPLV = 6.689 | COPc = IPLV =
[5 empty] | ≥ 264 and < 528 |  | Path B (typ part load operation), Capacity ≥ 264 and < 528 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path B (typ part load operation), Capacity ≥ 264 and < 528 kW | COPc = 4.459 IPLV = 6.825 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 4.918 IPLV = 7.601 | COPc = IPLV =
[5 empty] | ≥ 1 055 and < 2 110 |  | Path B (typ part load operation), Capacity ≥ 1 055 and < 2 110 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path B (typ part load operation), Capacity ≥ 1 055 and < 2 110 kW | COPc = 5.351 IPLV = 8.157 | COPc = IPLV =
[5 empty] | ≥ 2 110 |  | Path B (typ part load operation), Capacity ≥ 2 110 kW | Water-source heat pumps and heat recovery chillers, rotary screw, scroll, or reciprocating compressor, in cooling mode. Path B (typ part load operation), Capacity ≥ 2 110 kW | COPc = 5.717 IPLV = 8.801 | COPc = IPLV =
|  |  |  | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode | < 264 |  | Path B (typ part load operation), Capacity < 264 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path B (typ part load operation), Capacity < 264 kW | COPc = 4.812 IPLV = 7.601 | COPc = IPLV =
[5 empty] | ≥ 264 and < 528 |  | Path B (typ part load operation), Capacity ≥ 264 and < 528 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path B (typ part load operation), Capacity ≥ 264 and < 528 kW | COPc = 5.267 IPLV = 6.361 | COPc = IPLV =
[5 empty] | ≥ 528 and < 1 055 |  | Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path B (typ part load operation), Capacity ≥ 528 and < 1 055 kW | COPc = 5.621 IPLV = 8.567 | COPc = IPLV =
[5 empty] | ≥ 1 055 |  | Path B (typ part load operation), Capacity ≥ 1 055 kW | Water-source heat pumps and heat recovery chillers, centrifugal compressor, in cooling mode. Path B (typ part load operation), Capacity ≥ 1 055 kW | COPc = 5.717 IPLV = 8.801 | COPc = IPLV =
|  |  | Table 5.2.12.1.-M | Air-source heat pumps, in heating mode | > 0 | LWT = 40ºC, EAT = 8ºC db / 6ºC wb | RC: LWT = 40ºC, EAT = 8ºC db / 6ºC wb. Capacity > 0 kW | Air-source heat pumps, in heating mode. RC: LWT = 40ºC, EAT = 8ºC db / 6ºC wb. Capacity > 0 kW | COPh = 3.350 | COPh =
[5 empty] | > 0 | LWT = 40ºC, EAT = –8ºC db / –9ºC wb | RC: LWT = 40ºC, EAT = –8ºC db / –9ºC wb. Capacity > 0 kW | Air-source heat pumps, in heating mode. RC: LWT = 40ºC, EAT = –8ºC db / –9ºC wb. Capacity > 0 kW | COPh = 2.250 | COPh =
|  |  |  | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode | < 1 055 | LWT = 40ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | COPh = 4.760 | COPh =
[5 empty] | < 1 055 | LWT = 40ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | No reqm't
[5 empty] | ≥ 1 055 | LWT = 40ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | COPh = 5.060 | COPh =
[5 empty] | ≥ 1 055 | LWT = 40ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | No reqm't
|  |  |  | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes | < 1 055 | LWT = 40ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | COPhr = 8.550 | COPhr =
[5 empty] | < 1 055 | LWT = 40ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | No reqm't
[5 empty] | ≥ 1 055 | LWT = 40ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 40ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | COPhr = 9.140 | COPhr =
[5 empty] | ≥ 1 055 | LWT = 40ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 40ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | No reqm't
|  |  |  | Air-source heat pumps, in heating mode | > 0 | LWT = 50ºC, EAT = 8ºC db / 6ºC wb | RC: LWT = 50ºC, EAT = 8ºC db / 6ºC wb. Capacity > 0 kW | Air-source heat pumps, in heating mode. RC: LWT = 50ºC, EAT = 8ºC db / 6ºC wb. Capacity > 0 kW | COPh = 2.720 | COPh =
[5 empty] | > 0 | LWT = 50ºC, EAT = –8ºC db / –9ºC wb | RC: LWT = 50ºC, EAT = –8ºC db / –9ºC wb. Capacity > 0 kW | Air-source heat pumps, in heating mode. RC: LWT = 50ºC, EAT = –8ºC db / –9ºC wb. Capacity > 0 kW | COPh = 1.920 | COPh =
|  |  |  | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode | < 1 055 | LWT = 50ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | COPh = 3.610 | COPh =
[5 empty] | < 1 055 | LWT = 50ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | No reqm't
[5 empty] | ≥ 1 055 | LWT = 50ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | COPh = 3.880 | COPh =
[5 empty] | ≥ 1 055 | LWT = 50ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | No reqm't
|  |  |  | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes | < 1 055 | LWT = 50ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | COPhr = 6.290 | COPhr =
[5 empty] | < 1 055 | LWT = 50ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | No reqm't
[5 empty] | ≥ 1 055 | LWT = 50ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 50ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | COPhr = 6.850 | COPhr =
[5 empty] | ≥ 1 055 | LWT = 50ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 50ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | No reqm't
|  |  |  | Air-source heat pumps, in heating mode | > 0 | LWT = 60ºC, EAT = 8ºC db / 6ºC wb | RC: LWT = 60ºC, EAT = 8ºC db / 6ºC wb. Capacity > 0 kW | Air-source heat pumps, in heating mode. RC: LWT = 60ºC, EAT = 8ºC db / 6ºC wb. Capacity > 0 kW | COPh = 2.330 | COPh =
[5 empty] | > 0 | LWT = 60ºC, EAT = –8ºC db / –9ºC wb | RC: LWT = 60ºC, EAT = –8ºC db / –9ºC wb. Capacity > 0 kW | Air-source heat pumps, in heating mode. RC: LWT = 60ºC, EAT = –8ºC db / –9ºC wb. Capacity > 0 kW | COPh = 1.640 | COPh =
|  |  |  | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode | < 1 055 | LWT = 60ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | COPh = 2.660 | COPh =
[5 empty] | < 1 055 | LWT = 60ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | COPh = 3.530 | COPh =
[5 empty] | ≥ 1 055 | LWT = 60ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | COPh = 2.950 | COPh =
[5 empty] | ≥ 1 055 | LWT = 60ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | Water-source heat pumps, rotary screw, scroll, reciprocating or centrifugal compressor, in heating mode. RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | COPh = 3.870 | COPh =
|  |  |  | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes | < 1 055 | LWT = 60ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity < 1 055 kW | COPhr = 4.390 | COPhr =
[5 empty] | < 1 055 | LWT = 60ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity < 1 055 kW | COPhr = 6.100 | COPhr =
[5 empty] | ≥ 1 055 | LWT = 60ºC, EST / LST = 12ºC / 7ºC | RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 60ºC, EST / LST = 12ºC / 7ºC. Capacity ≥ 1 055 kW | COPhr = 4.960 | COPhr =
[5 empty] | ≥ 1 055 | LWT = 60ºC, EST / LST = 24ºC / 19ºC | RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | Heat-recovery chillers, rotary screw, scroll, reciprocating or centrifugal compressor, simultaneous heating and cooling modes. RC: LWT = 60ºC, EST / LST = 24ºC / 19ºC. Capacity ≥ 1 055 kW | COPhr = 6.800 | COPhr =
|  |  | Table 5.2.12.1.-N | Electric | < 88 |  | Capacity < 88 kW | Electric. Capacity < 88 kW | Must include auto water temp control | Y/N?
[5 empty] | ≥ 88 |  | Capacity ≥ 88 kW | Electric. Capacity ≥ 88 kW | No reqm't
|  |  |  | Gas-fired | < 88 |  | Capacity < 88 kW | Gas-fired. Capacity < 88 kW | AFUE = 90% (water) AFUE = 82% (steam) | AFUE = AFUE =
[5 empty] | ≥ 88 and < 733 |  | Capacity ≥ 88 and < 733 kW | Gas-fired. Capacity ≥ 88 and < 733 kW | Et ≥ 90% (water) Et ≥ 81% (steam) | Et = Et =
[5 empty] | ≥ 733 and < 2 930 |  | Capacity ≥ 733 and < 2 930 kW | Gas-fired. Capacity ≥ 733 and < 2 930 kW | Ec ≥ 90% (water) Et ≥ 82% (steam) | Ec = Et =
|  |  |  | Oil-fired | < 88 |  | Capacity < 88 kW | Oil-fired. Capacity < 88 kW | AFUE = 86% (water) AFUE = 85% (steam) | AFUE = AFUE =
[5 empty] | ≥ 88 and < 733 |  | Capacity ≥ 88 and < 733 kW | Oil-fired. Capacity ≥ 88 and < 733 kW | Et = 87% (water) Et = 84% (steam) | Et = Et =
[5 empty] | ≥ 733 and < 2 930 |  | Capacity ≥ 733 and < 2 930 kW | Oil-fired. Capacity ≥ 733 and < 2 930 kW | Ec = 88% (water) Et = 85% (steam) | Ec = Et =
|  |  | Table 5.2.12.1.-O | Electric furnaces | < 66 |  | Capacity < 66 kW | Electric furnaces. Capacity < 66 kW | FER = 0.044 × Qmax + 165 | FER =
[5 empty] | ≥ 66 |  | Capacity ≥ 66 kW | Electric furnaces. Capacity ≥ 66 kW | No reqm't
|  |  |  | Gas-fired warm-air furnaces | ≤ 66 | Without integrated cooling | Capacity ≤ 66 kW. RC: Without integrated cooling | Gas-fired warm-air furnaces. Capacity ≤ 66 kW. RC: Without integrated cooling | AFUE = 95% FER = 0.044 × Qmax + 195 | AFUE = FER =
[5 empty] | ≤ 66 | Outdoor furnaces with integrated cooling | Capacity ≤ 66 kW. RC: Outdoor furnaces with integrated cooling | Gas-fired warm-air furnaces. Capacity ≤ 66 kW. RC: Outdoor furnaces with integrated cooling | AFUE = 78% FER = 0.044 × Qmax + 199 | AFUE = FER =
[5 empty] | ≤ 66 | Through-the-wall, with integrated cooling | Capacity ≤ 66 kW. RC: Through-the-wall, with integrated cooling | Gas-fired warm-air furnaces. Capacity ≤ 66 kW. RC: Through-the-wall, with integrated cooling | AFUE = 90% FER = 0.044 × Qmax + 195 | AFUE = FER =
[5 empty] | ≤ 66 | Three-phase electric supply | Capacity ≤ 66 kW. RC: Three-phase electric supply | Gas-fired warm-air furnaces. Capacity ≤ 66 kW. RC: Three-phase electric supply | AFUE = 78% or Et = 80% | AFUE = Et =
[5 empty] | > 66 and ≤ 117 |  | Capacity > 66 and ≤ 117 kW | Gas-fired warm-air furnaces. Capacity > 66 and ≤ 117 kW | Et = 81% | Et =
|  |  |  | Gas-fired packaged furnaces | ≤ 2 931 |  | Capacity ≤ 2 931 kW | Gas-fired packaged furnaces. Capacity ≤ 2 931 kW | Et = 80% | Et =
|  |  |  | Gas-fired duct furnaces | ≤ 2 931 |  | Capacity ≤ 2 931 kW | Gas-fired duct furnaces. Capacity ≤ 2 931 kW | Et = 81% | Et =
|  |  |  | Gas-fired unit heaters | ≤ 2 931 |  | Capacity ≤ 2 931 kW | Gas-fired unit heaters. Capacity ≤ 2 931 kW | Et = 82% | Et =
|  |  |  | Oil-fired warm-air furnaces | ≤ 66 |  | Capacity ≤ 66 kW | Oil-fired warm-air furnaces. Capacity ≤ 66 kW | Et = 84.5% AFUE = 85% | Et = AFUE =
[5 empty] | > 66 |  | Capacity > 66 kW | Oil-fired warm-air furnaces. Capacity > 66 kW | Et = 82% | Et =
|  |  |  | Oil-fired duct furnaces and unit heaters | > 0 |  | Capacity > 0 kW | Oil-fired duct furnaces and unit heaters. Capacity > 0 kW | Et = 81% | Et =
|  |  | Table 5.2.12.1.-P | Gas-fired fireplaces and stoves, non-decorative | > 0 |  | Capacity > 0 kW | Gas-fired fireplaces and stoves, non-decorative. Capacity > 0 kW | FE = 50%, with direct vent and without standing pilot light | FE =
|  |  |  | Solid-fuel-burning stoves | > 0 |  | Capacity > 0 kW | Solid-fuel-burning stoves. Capacity > 0 kW | No reqm't
|  |  |  | Solid-fuel-burning boilers | < 2 000 |  | Capacity < 2 000 kW | Solid-fuel-burning boilers. Capacity < 2 000 kW | No reqm't
|  |  |  | Gas-fired infrared heaters, high-intensity | ≤ 117 kW per burner |  | Capacity ≤ 117 kW per burner | Gas-fired infrared heaters, high-intensity. Capacity ≤ 117 kW per burner | NRE ≥ 55% | NRE =
|  |  |  | Gas-fired infrared heaters, tubular and low-intensity | ≤ 117 kW per burner |  | Capacity ≤ 117 kW per burner | Gas-fired infrared heaters, tubular and low-intensity. Capacity ≤ 117 kW per burner | NRE ≥ 45% | NRE =
|  |  | Table 5.2.12.2. | Cooling tower / fluid cooler: centrifugal fan, direct-contact | > 0 | 35°C entering water, 29.4°C leaving water, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: 35°C entering water, 29.4°C leaving water, 23.9°C wet bulb | Cooling tower / fluid cooler: centrifugal fan, direct-contact. Rejection Capacity > 0 kW. RC: 35°C entering water, 29.4°C leaving water, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.026 | E/T Ratio =
|  |  |  | Cooling tower / fluid cooler: propeller or axial fan, direct-contact | > 0 | 35°C entering water, 29.4°C leaving water, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: 35°C entering water, 29.4°C leaving water, 23.9°C wet bulb | Cooling tower / fluid cooler: propeller or axial fan, direct-contact. Rejection Capacity > 0 kW. RC: 35°C entering water, 29.4°C leaving water, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.013 | E/T Ratio =
|  |  |  | Cooling tower / fluid cooler: centrifugal fan, indirect-contact evaporative | > 0 | 38.9°C entering water, 32.2°C leaving water, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: 38.9°C entering water, 32.2°C leaving water, 23.9°C wet bulb | Cooling tower / fluid cooler: centrifugal fan, indirect-contact evaporative. Rejection Capacity > 0 kW. RC: 38.9°C entering water, 32.2°C leaving water, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.061 | E/T Ratio =
|  |  |  | Cooling tower / fluid cooler: propeller or axial fan, indirect-contact evaporative | > 0 | 38.9°C entering water, 32.2°C leaving water, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: 38.9°C entering water, 32.2°C leaving water, 23.9°C wet bulb | Cooling tower / fluid cooler: propeller or axial fan, indirect-contact evaporative. Rejection Capacity > 0 kW. RC: 38.9°C entering water, 32.2°C leaving water, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.026 | E/T Ratio =
|  |  |  | Cooling tower / fluid cooler: propeller or axial fan, dry | > 0 | 46.1°C entering water, 40.6°C leaving water, 35°C dry bulb | Rejection Capacity > 0 kW. RC: 46.1°C entering water, 40.6°C leaving water, 35°C dry bulb | Cooling tower / fluid cooler: propeller or axial fan, dry. Rejection Capacity > 0 kW. RC: 46.1°C entering water, 40.6°C leaving water, 35°C dry bulb | Elect/Thermal Ratio ≤ 0.113 | E/T Ratio =
|  |  |  | Condenser: centrifugal fan, indirect-contact evaporative | > 0 | R-717 test fluid: 35.7°C condensing temperature, 60°C entering gas temperature, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: R-717 test fluid: 35.7°C condensing temperature, 60°C entering gas temperature, 23.9°C wet bulb | Condenser: centrifugal fan, indirect-contact evaporative. Rejection Capacity > 0 kW. RC: R-717 test fluid: 35.7°C condensing temperature, 60°C entering gas temperature, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.023 | E/T Ratio =
[5 empty] | > 0 | R-448A test fluid: 40.6°C condensing temperature, 73.9°C entering gas temperature, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: R-448A test fluid: 40.6°C condensing temperature, 73.9°C entering gas temperature, 23.9°C wet bulb | Condenser: centrifugal fan, indirect-contact evaporative. Rejection Capacity > 0 kW. RC: R-448A test fluid: 40.6°C condensing temperature, 73.9°C entering gas temperature, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.019 | E/T Ratio =
|  |  |  | Condenser: propeller or axial fan, indirect-contact evaporative | > 0 | R-717 test fluid: 35.7°C condensing temperature, 60°C entering gas temperature, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: R-717 test fluid: 35.7°C condensing temperature, 60°C entering gas temperature, 23.9°C wet bulb | Condenser: propeller or axial fan, indirect-contact evaporative. Rejection Capacity > 0 kW. RC: R-717 test fluid: 35.7°C condensing temperature, 60°C entering gas temperature, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.019 | E/T Ratio =
[5 empty] | > 0 | R-448A test fluid: 40.6°C condensing temperature, 73.9°C entering gas temperature, 23.9°C wet bulb | Rejection Capacity > 0 kW. RC: R-448A test fluid: 40.6°C condensing temperature, 73.9°C entering gas temperature, 23.9°C wet bulb | Condenser: propeller or axial fan, indirect-contact evaporative. Rejection Capacity > 0 kW. RC: R-448A test fluid: 40.6°C condensing temperature, 73.9°C entering gas temperature, 23.9°C wet bulb | Elect/Thermal Ratio ≤ 0.016 | E/T Ratio =
|  |  |  | Condenser: air-cooled | > 0 | 51.7°C condensing temperature, 87.8°C entering gas temperature, 8.3°C subcooling 35°C dry bulb | Rejection Capacity > 0 kW. RC: 51.7°C condensing temperature, 87.8°C entering gas temperature, 8.3°C subcooling 35°C dry bulb | Condenser: air-cooled. Rejection Capacity > 0 kW. RC: 51.7°C condensing temperature, 87.8°C entering gas temperature, 8.3°C subcooling 35°C dry bulb | Elect/Thermal Ratio ≤ 0.015 | E/T Ratio =

## Code Tables (hidden)
Part 3
| Table 3.2.2.2. | [15 empty] | Table 3.2.2.4. | [22 empty] | Table 3.2.3.1
| Above Ground Opaque Building Assembly | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 |  | Component | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 |  | Component | [16 empty] | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 | Assemblies in Contact with the Ground | Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000
| Wall | 0.29 | 0.278 | 0.247 | 0.21 | 0.21 | 0.183 |  | Fenestration | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6 |  | All Doors | [16 empty] | 2.4 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6 | Walls | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Roof | 0.164 | 0.183 | 0.183 | 0.162 | 0.162 | 0.142 | [32 empty] | Roofs | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Floor | 0.193 | 0.183 | 0.183 | 0.162 | 0.162 | 0.142 | [32 empty] | Floors | 0.757 | 0.757 | 0.757 | 0.757 | 0.757 | 0.379
| Fenestration | 1.9 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6
| Doors | 2.12 | 2.2 | 2.2 | 2.2 | 2.2 | 1.6
| Underground Walls | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Underground Roofs | 0.568 | 0.379 | 0.284 | 0.284 | 0.284 | 0.21
| Underground Floors | 0.757 | 0.757 | 0.757 | 0.757 | 0.757 | 0.379
| FDWR Requirements Article 3.2.1.4. | [14 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
| Zone 4: <3000 | Zone 5: 3000 to 3999 | Zone 6: 4000 to 4999 | Zone 7A: 5000 to 5999 | Zone 7B: 6000 to 6999 | Zone 8: ≥ 7000 |  | Lighting Power Density by Building Type for Use with the Building Area Method (Forming Part of Sentences 4.2.1.5.(1), (4) and (5)) | [7 empty] | 1: Table 6.2.2.1.; 4: SL (top inlet); 6: SL (bottom inlet); 8: SL (top inlet); 10: SL (bottom inlet); 12: SL (w division); 14: EF; 15: Et (& instant); 16: Et and SL (w Q & sq root Vr) combo; 19: UEF (w FHR and Vs)
1 | 0.4 | 0.4 | 0.47 | 0.47 | 0.47 | 0.2 |  | Building Type | Lighting Power Density, W/m2 | [5 empty] | 1 | 1: Electric, storage-type; Input ≤ 12 kW; Capacity 50 ≤ Vr < 270 L; 2: SL ≤ 40 + 0.20Vr (bottom inlet); SL ≤ 35 + 0.20Vr (top inlet); 3: SL ≤ SL ≤; 4: 35; 5: 0.2; 6: 40; 7: 0.2; 21: SL = SL =
[8 empty] | Automotive facility | 8.1 | [5 empty] | 2 | 1: Electric, storage-type; Input ≤ 12 kW; Capacity 270 ≤ Vr < 454 L; 2: SL ≤ 0.472Vr - 33.5 (bottom inlet); SL ≤ 0.472Vr - 38.5 (top inlet); 3: SL ≤ SL ≤; 8: 0.472; 9: 38.5; 10: 0.472; 11: 33.5; 21: SL = SL =
[8 empty] | Convention centre | 6.9 | [5 empty] | 3 | 1: Electric, storage-type; Input > 12 kW; ΔT = 44.4°C; 2: SL ≤ 0.3 +102.2/Vr; 3: SL ≤; 12: 0.3; 13: 102.2; 21: SL =
[8 empty] | Courthouse | 8.5 | [5 empty] | 4 | 1: Electric, storage-type, heat pump; Input ≤ 24A and ≤ 250 V; 2: EF ≥ 2.1; 3: EF ≥; 14: 2.1; 21: EF =
[8 empty] | Dining: bar lounge/leisure | 8.6 | [5 empty] | 5 | 1: Electric, instantaneous;; 2: typically approaches 100% efficiency; 3: Et ≥; 15: 98; 21: Et =
[8 empty] | Dining: cafeteria/fast food | 8.2 | [5 empty] | 6 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; FHR < 68; 2: UEF ≥ 0.3456 - (0.00053 Vs); 3: UEF ≥; 19: 0.3456; 20: 0.00053; 21: UEF =
[8 empty] | dining: family | 7.6 | [5 empty] | 7 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; 68 ≤ FHR < 193; 2: UEF ≥ 0.5982 - (0.00050 Vs); 3: UEF ≥; 19: 0.5982; 20: 0.0005; 21: UEF =
[8 empty] | Dormitory | 5.7 | [5 empty] | 8 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; 193 ≤ FHR < 284; 2: UEF ≥ 0.6483 - (0.00045 Vs); 3: UEF ≥; 19: 0.6483; 20: 0.00045; 21: UEF =
[8 empty] | Exercise centre | 7.8 | [5 empty] | 9 | 1: Gas-fired, storage type; Input ≤ 22 kW; 76 ≤ Vs < 208 L; FHR ≥ 284; 2: UEF ≥ 0.6920 - (0.00034 Vs); 3: UEF ≥; 19: 0.692; 20: 0.00034; 21: UEF =
[8 empty] | Fire station | 6 | [5 empty] | 10 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; FHR < 68; 2: UEF ≥ 0.6470 - (0.00016 Vs); 3: UEF ≥; 19: 0.647; 20: 0.00016; 21: UEF =
[8 empty] | Gymnasium | 8.2 | [5 empty] | 11 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; 68 ≤ FHR < 193; 2: UEF ≥ 0.7689 - (0.00013 Vs); 3: UEF ≥; 19: 0.7689; 20: 0.00013; 21: UEF =
[8 empty] | Health care clinic | 8.7 | [5 empty] | 12 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; 193 ≤ FHR < 284; 2: UEF ≥ 0.7897 - (0.00011 Vs); 3: UEF ≥; 19: 0.7897; 20: 0.00011; 21: UEF =
[8 empty] | Hospital | 10.3 | [5 empty] | 13 | 1: Gas-fired, storage type; Input ≤ 22 kW; 208 ≤ Vs < 380 L; FHR ≥ 284; 2: UEF ≥ 0.8072 - (0.00008 Vs); 3: UEF ≥; 19: 0.8072; 20: 8e-05; 21: UEF =
[8 empty] | Hotel/Motel | 6 | [5 empty] | 14 | 1: Gas-fired, storage type; 22 kW < Input ≤ 30.5 kW; Capacity Vr ≤ 454 L; FHR > 0; 2: UEF ≥ 0.8107 - (0.00021 Vs); 3: UEF ≥; 19: 0.8107; 20: 0.00021; 21: UEF =
[8 empty] | Library | 8.9 | [5 empty] | 15 | 1: Gas-fired, storage type; All other Input Powers; ΔT = 50°C; 2: Et ≥ 78% SL ≤ (1.25 Q) + (16.57 √Vr); 3: Et ≥ SL ≤; 16: 78; 17: 1.25; 18: 16.57; 21: Et = SL =
[8 empty] | Manufacturing facility | 8.9 | [5 empty] | 16 | 1: Gas-fired, instant's; < 59 kW; Capacity Vr ≤ 7.6 L; Input/Vs ≥ 310 W/L; < 6.4 L/min; 2: UEF ≥ 0.86; 3: UEF ≥; 19: 0.86; 20: 0; 21: UEF =
[8 empty] | Motion picture theatre | 4.7 | [5 empty] | 17 | 1: Gas-fired, instant's; < 59 kW; Capacity Vr ≤ 7.6 L; Input/Vs ≥ 310 W/L; ≥ 6.4 L/min; 2: UEF ≥ 0.87; 3: UEF ≥; 19: 0.87; 20: 0; 21: UEF =
[8 empty] | Multi-unit residential building | 4.8 | [5 empty] | 18 | 1: Gas-fired, instantaneous; All other Input Powers; Input/Vs ≥ 310 W/L; 2: Et ≥ 94%; 3: Et ≥; 15: 94; 21: Et =
[8 empty] | Museum | 5.9 | [5 empty] | 19 | 1: Solar Thermal Service Water Heaters; Electric back-up; All Capacities; 2: SEF ≥ 1.4; 3: SEF ≥; 14: 1.4; 21: SEF =
[8 empty] | Office | 6.9 | [5 empty] | 20 | 1: Solar Thermal Service Water Heaters; Gas-fired back-up; All Capacities; 2: SEF ≥ 0.9; 3: SEF ≥; 14: 0.9; 21: SEF =
[8 empty] | Penitentiary | 7.4 | [5 empty] | 21 | 1: Pool Heaters, gas-fired; Input < 117.2 kW; 2: Et ≥ 82%; 3: Et ≥; 15: 82; 21: Et =
[8 empty] | Performing arts theatre | 9 | [5 empty] | 22 | 1: Pool Heaters, oil-fired; 2: Et ≥ 78%; 3: Et ≥; 15: 78; 21: Et =
[8 empty] | Police station | 7.1 | [5 empty] | 23 | 1: Pool Heaters, heat pump; Outdoor air 10°C db / 6.8°C wb; 26.7°C entering water; 2: ≥ 4.0 COP; 3: COP ≥; 15: 4.0 COP; 21: COP =
[8 empty] | Post office | 7 | [5 empty] | 24 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; 2: EF ≥ 0.68 - (0.0005 Vr); 3: EF ≥; 19: 0.68; 20: 0.0005; 21: EF =
[8 empty] | Religious building | 7.2 | [5 empty] | 25 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; FHR < 68; 2: UEF ≥ 0.2509 - (0.00032 Vs); 3: UEF ≥; 19: 0.2509; 20: 0.00032; 21: UEF =
[8 empty] | Retail area | 9 | [5 empty] | 26 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; 68 ≤ FHR < 193; 2: UEF ≥ 0.5330 - (0.00042 Vs); 3: UEF ≥; 19: 0.533; 20: 0.00042; 21: UEF =
[8 empty] | School/university | 7.8 | [5 empty] | 27 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr > 76 L; 193 ≤ FHR < 284; 2: UEF ≥ 0.6078 - (0.00042 Vs); 3: UEF ≥; 19: 0.6078; 20: 0.00042; 21: UEF =
[8 empty] | Sports arena | 8.2 | [5 empty] | 28 | 1: Oil-fired, storage type; Input ≤ 30.5 kW; Capacity Vr ≤ 76 L; FHR ≥ 284; 2: UEF ≥ 0.6815 - (0.00037 Vs); 3: UEF ≥; 19: 0.6815; 20: 0.00037; 21: UEF =
[8 empty] | Storage garage | 1.9 | [5 empty] | 29 | 1: Oil-fired, storage type; 30.5 kW< Input ≤ 41 kW; Vr ≤ 454 L; Input/Vs < 310 W/L; FHR > 0; 2: UEF ≥ 0.6740 - (0.00035 Vs); 3: UEF ≥; 19: 0.674; 20: 0.00035; 21: UEF =
[8 empty] | Town hall | 7.4 | [5 empty] | 30 | 1: Oil-fired, storage type; All other Input Powers; 2: Et ≥ 80% SL ≤ (1.25 Q) + (16.57 √Vr); 3: Et ≥ SL ≤; 16: 80; 17: 1.25; 18: 16.57; 21: Et = SL =
[8 empty] | Transportation facility | 5.4 | [5 empty] | 31 | 1: Oil-fired, instantaneous; Input ≤ 61.5 kW; 2: EF ≥ 0.59 - (0.0005 Vr); 3: EF ≥; 19: 0.59; 20: 0.0005; 21: EF =
[8 empty] | Warehouse | 4.8 | [5 empty] | 32 | 1: Oil-fired, instant's; Input Others; Vr < 37.8 L; Input/Vs ≥ 310 W/L; 2: Et ≥ 80%; 3: Et ≥; 15: 80; 21: Et =
[8 empty] | Workshop | 9.8 | [5 empty] | 33 | 1: Oil-fired, instant's; Input Others; Vr ≥ 37.8 L; Input/Vs ≥ 310 W/L; ΔT = 50°C; 2: Et ≥ 78% SL ≤ (1.25 Q) + (16.57 √Vr); 3: Et ≥ SL ≤; 16: 78; 17: 1.25; 18: 16.57; 21: Et = SL =
Lighting Power Density by Space Type for Use with Space by Space Method
[8 empty] | Space Type | Lighting Power Density, W/m2
[8 empty] | Atrium < 6 m in height | 4.2
[8 empty] | Atrium between 6 m and 12 m in height | 5.2
[8 empty] | Atrium > 12 m in height | 6.5
[8 empty] | Audience seating area – permanent for auditorium | 6.5
Audience seating area – permanent for convention centre
[8 empty] | Audience seating area – permanent for gymnasium | 2.5
[8 empty] | Audience seating area – permanent for motion picture theatre | 2.9
[8 empty] | Audience seating area – permanent for penitentiary | 7.2
[8 empty] | Audience seating area – permanent for performing arts theatre | 12.5
[8 empty] | Audience seating area – permanent for religious building | 7.8
[8 empty] | Audience seating area – permanent for sports arena | 3.5
[8 empty] | Audience seating area – permanent other | 2.5
[8 empty] | Banking activity area and offices | 6.5
[8 empty] | Classroom/Lecture hall/Training room for penitentiary | 9.5
[8 empty] | Classroom/Lecture hall/Training room other | 7.6
[8 empty] | Computer/Server room | 10.1
[8 empty] | Conference/Meeting/ Multi-purpose room | 10.5
[8 empty] | Confinement cell | 7.5
[8 empty] | Copy/Print room | 3.3
[8 empty] | Corridor/Transition area for hospital | 7.7
[8 empty] | Corridor/Transition area for manufacturing facility | 3.1
[8 empty] | Corridor/Transition area for space designed to ANSI/IES RP-28 (and used primarily by residents) | 7.7
[8 empty] | Corridor/Transition area other | 4.4
[8 empty] | Courtroom | 12.9
[8 empty] | Dining area for bar lounge/leisure dining | 9.3
[8 empty] | Dining area for cafeteria/fast food dining | 4.3
[8 empty] | Dining area for family dining | 6.5
[8 empty] | Dining area for penitentiary | 4.5
[8 empty] | Dining area for space designed to ANSI/IES RP-28 (and used primarily by residents) | 13.7
[8 empty] | Dining area other | 4.7
[8 empty] | Dressing/Fitting room for performing arts theatre | 4.4
[8 empty] | Electrical/Mechanical room | 4.6
[8 empty] | Emergency vehicle garage | 5.6
[8 empty] | Food preparation area | 11.7
[8 empty] | Guest room | 4.4
[8 empty] | Laboratory for classroom | 11.9
[8 empty] | Laboratory other | 14.3
[8 empty] | Laundry/Washing area | 5.7
[8 empty] | Loading dock – interior | 9.5
[8 empty] | Lobby for elevator | 7
[8 empty] | Lobby for hotel | 5.4
[8 empty] | Lobby for motion picture theatre | 2.5
[8 empty] | Lobby for performing arts theatre | 13.5
[8 empty] | Lobby for space designed to ANSI/IES RP-28 (and used primarily by residents) | 18.2
[8 empty] | Lobby other | 9
[8 empty] | Locker room | 5.6
[8 empty] | Lounge/Break room for health care facility | 4.5
[8 empty] | Lounge/Break room other | 6.3
[8 empty] | Office enclosed, ≤ 25 sqm | 8
[8 empty] | Office enclosed, > 25 sqm | 7.1
[8 empty] | Office open plan | 6.6
[8 empty] | Pharmacy area | 17.9
[8 empty] | Sales area | 11.3
[8 empty] | Seating area – general | 2.5
[8 empty] | Stairway | The LPD and lighting control requirements for a stairway shall be the same as those for the space containing the stairway.
[8 empty] | Stairwell | 5.3
[8 empty] | Storage garage – interior | 1.5
[8 empty] | Storage room < 5 sqm | 5.5
[8 empty] | Storage room ≥ 5 sqm | 4.1
[8 empty] | Vehicle maintenance area | 6.5
[8 empty] | Washroom for space designed to ANSI/IES RP-28 (and used primarily by residents) | 13.5
[8 empty] | Washroom other | 6.8
[8 empty] | Workshop | 13.5
[8 empty] | Convention centre – exhibit space | 6.6
[8 empty] | Dormitory – living quarters | 5.4
[8 empty] | Fire station – sleeping quarters | 2.5
[8 empty] | Gymnasium/Fitness centre exercise area | 9.6
[8 empty] | Gymnasium/Fitness centre playing area | 9.2
[8 empty] | Health care facility exam/treatment room | 15.1
[8 empty] | Health care facility imaging room | 10.1
[8 empty] | Health care facility medical supply room | 6.7
[8 empty] | Health care facility nursery | 9.9
[8 empty] | Health care facility nurses' station | 12.6
[8 empty] | Health care facility operating room | 24.3
[8 empty] | Health care facility patient room | 7.3
[8 empty] | Health care facility physical therapy room | 9.8
[8 empty] | Health care facility recovery room | 13.5
[8 empty] | Library reading area | 10.3
[8 empty] | Library stacks | 12.7
[8 empty] | Manufacturing facility detailed manufacturing area | 8.6
[8 empty] | Manufacturing facility equipment room | 8.2
[8 empty] | Manufacturing facility extra high bay area (> 15 m floor-to-ceiling height) | 15.3
[8 empty] | Manufacturing facility high bay area (7.5 m to 15 m floor-to-ceiling height) | 13.4
[8 empty] | Manufacturing facility low bay area (< 7.5 m floor-to-ceiling height) | 9.3
[8 empty] | Museum general exhibition area | 3.3
[8 empty] | Museum restoration room | 11.9
[8 empty] | Post office – sorting area | 8.1
[8 empty] | Religious building fellowship hall | 5.8
[8 empty] | Religious building worship/pulpit/choir area | 9.2
[8 empty] | Retail facility dressing/fitting room | 5.4
[8 empty] | Retail facility mall concourse | 8.8
[8 empty] | Space designed to ANSI/IES RP-28 chapel (used primarily by residents) | 7.5
[8 empty] | Space designed to ANSI/IES RP-28 recreation room (used primarily by residents) | 19
[8 empty] | Sports arena – playing area Class I facility | 31.6
[8 empty] | Sports arena – playing area Class II facility | 21.6
[8 empty] | Sports arena – playing area Class III facility | 13.9
[8 empty] | Sports arena – playing area Class IV facility | 9.3
[8 empty] | Transportation facility airport concourse | 2.7
[8 empty] | Transportation facility baggage/carousel area | 4.2
[8 empty] | Transportation facility terminal ticket counter | 5.5
[8 empty] | Warehouse – storage area medium to bulky palletized items | 3.6
[8 empty] | Warehouse – storage area small hand-carried items | 7.4

## NECB-ZEBP Checklist - First TI
Energy Checklist for First TIs within NECB/ZEBP Buildings
Building Use description will appear here.
Building Address : | [17 empty] | Building Permit Application No.:
Tenancy Address :
This form is to be completed digitally. For ease of use, drop boxes and pop-up instructions are included.
IMPORTANT - Submission Format and Process:
Effective September 15, 2025, this First TI checklist is to be completed and submitted at the Building Permit application stage. Submit online with your Building Permit application. Include all relevent documents pertaining to scope of work.
Space Use, Area & Performance Information
| Primary Use/Area: | [13 empty] | TI Space(s) | Non-residential Cond'd Space Area (m2):
| Second Use/Area: | [14 empty] | Resid Cond'd Common Space Area (m2):
| Tertiary Use/Area: | [14 empty] | Semiheated Space Area (m2):
| Total Area (m2): |  |  |  |  | Building Use Description | [9 empty] | Is public access via an outdoor entrance?
Is existing outdoor entrance being modified?
Neighbourhood Energy (N/E) Systems
| Rz Cond's |  | EUI required: | [5 empty] | Energy reduction: |  |  |  |  | LEED ver: |  |  |  | LEED targets:
|  |  | achieved: | [6 empty] | achieved: | [8 empty] | achieved:
Renewable / High Performance Energy Systems
- Renewable Energy systems:
- High Performance Energy systems:
If within a Neighbourhood Energy area, indicate which system:
| Base Building's N/E status: | [17 empty] | TI's thermal energy requirement: | N/A
| VBBL (10.2.1.2/10.2.1.3) - Deliverables for NECB/ZEBP First TIs | [21 empty] | Are Reg'd Professionals involved with this project?
10.2.2.19. - Does the proposed scope of work include the design and provision of exterior patio/space heating systems?
| NECB Part 3) Building Envelope | [21 empty] | Applicability:
|  |  |  | Building Envelope Compliance Table (tab below) | [11 empty] | Energy Statements on Drawings | [6 empty] | Dwg #:
| or; |  |  | Building Envelope Energy Perf Comparison Calc | [11 empty] | Complies with NECB Envelope Alterations (2.1.1)
| NECB Part 4) Lighting | [21 empty] | Applicability:
|  |  |  | Lighting Compliance Table (tab below) | [11 empty] | Energy Statements on Drawings | [6 empty] | Dwg #:
[16 empty] | Drawing: Reflected Ceiling Plan | [6 empty] | Dwg #:
| NECB Part 5) HVAC | [21 empty] | Applicability:
|  |  |  | HVAC Compliance Table (tab below) | [11 empty] | Energy Statements on Drawings | [6 empty] | Dwg #:
Source of Ventilation design:
Source of Operation Schedule:
| NECB Part 6) Service Water Htg | [21 empty] | Applicability:
|  |  |  | Service Water Htg Compliance Table (tab below) | [11 empty] | Energy Statements on Drawings | [6 empty] | Dwg #:
Electric/Gas Water Heating System is Allowed
OCCUPANCY PERMIT STAGE
| Check one only; | [5 empty] | Building Permit stage submission is complete and accurate - No Revisions Required | [6 empty] | OR |  | Submitting revised Deliverables (Submit only the documentation that differs from Building Permit stage Deliverables)
List All Revised and Resubmitted Deliverables Using Drop-Down Boxes Below;
|  | NECB Part | [8 empty] | Revised Documentation
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [16 empty] | DOC/2012/155502 |  |  |  | Version: |  | 250425-1
Drop Down Boxes
| Box 1 |  |  | Box 2 |  |  | Renewable Energy | [5 empty] | Box 4 | [5 empty] | Box 6 |  | N/E | [5 empty] | Box 8
| Yes |  |  | Yes |  |  | N/A | [5 empty] | X | [5 empty] | Yes |  | Use Base Building N/E System | [5 empty] | X
| No |  |  | No |  |  | Photovoltaic systems | [5 empty] | N/A | [5 empty] | N/A |  | None
|  |  |  | N/A |  |  | Solar Thermal systems | [13 empty] | N/A
Bio-fuel based energy
Geothermal Heating
Geothermal Electric
Low-impact Hydro Electric
Wave & Tidal Power
| LEED Version | [6 empty] | LEED Certif | [5 empty] | Building Use(s) |  |  |  |  | Building Use(s)
| N/A | [17 empty] | Building Use Description | [5 empty] | Building Use description will appear here.
| LEED v1.0 | [6 empty] | N/A | [5 empty] | Unknown (Core & Shell) |  |  |  |  | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
| LEED v1.1 | [6 empty] | Platinum | [5 empty] | Bank Branch |  |  |  |  | Bank Branch | [5 empty] | Bank Branch refers to a commercial banking outlet that offers banking services to walk-in customers. Gross Floor Area should include all space within the building(s), including banking areas, vaults, lobbies, atriums, kitchens used by staff, conference rooms, storage areas, stairways, and elevator shafts.
| LEED 2009 | [6 empty] | Gold | [5 empty] | Data Centre |  |  |  |  | Data Centre | [5 empty] | Data Center refers to buildings specifically designed and equipped to meet the needs of high density computing equipment, such as server racks, used for data storage and processing. Typically these facilities require dedicated uninterruptible power supplies and cooling systems. Data center functions may include traditional enterprise services, on-demand enterprise services, high performance computing, internet facilities, and/or hosting facilities. Often Data Centers are free standing, mission critical computing centers. When a data center is located within a larger building, it will usually have its own power and cooling systems, and require a constant power load of 75 kW or more. Data Center is intended for sophisticated computing and server functions; it should not be used to represent a server closet or computer training area. Gross Floor Area should include all space within the building(s) including raised floor computing space, server rack aisles, storage silos, control console areas, battery rooms, mechanical rooms for cooling equipment, administrative office areas, elevator shafts, stairways, break rooms and restrooms.
| LEED Mid Rise | [6 empty] | Silver | [5 empty] | Distribution Centre |  |  |  |  | Distribution Centre | [5 empty] | Distribution Center refers to unrefrigerated buildings that are used for the temporary storage and redistribution of goods, manufactured products, merchandise or raw materials. Gross Floor Area should include all space within the building(s) including space designed to store non-perishable goods and merchandise, offices, lobbies, stairways, rest rooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
| LEED v4 | [6 empty] | Certified | [5 empty] | Education (Adult C Educ) |  |  |  |  | Education (Adult C Educ) | [5 empty] | Adult Education refers to buildings used primarily for providing adult students with continuing education, workforce development, or professional development outside of the college or university setting. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, auditoriums, stairways, atriums, elevator shafts, and storage areas.
[14 empty] | Education (College/Univ) |  |  |  |  | Education (College/Univ) | [5 empty] | College/University refers to buildings used for the purpose of higher education. This includes public and private colleges and universities. Gross Floor Area should include all space within the building(s), including classrooms, laboratories, offices, cafeterias, maintenance facilities, arts facilities, athletic facilities, residential areas, storage rooms, restrooms, elevator shafts, and stairways.
[14 empty] | Education (K-12) |  |  |  |  | Education (K-12) | [5 empty] | K-12 School refers to buildings or campuses used as a school for Kindergarten through 12th grade students. This does not include college or university classroom facilities/laboratories, or vocational, technical, trade, adult, or continuing education schools. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, laboratory classrooms, portable classrooms, greenhouses, stairways, atriums, elevator shafts, small landscaping sheds, and storage areas. The ENERGY STAR score for K-12 School does not apply to preschool or day care buildings; in order to classify as K-12 school, more than 75% of the students must be in kindergarten or older.
| LEED Type | [12 empty] | Education (Pre/Daycare) |  |  |  |  | Education (Pre/Daycare) | [5 empty] | Pre-school/Daycare applies to buildings used for educational programs or daytime supervision/recreation for young children before they attend Kindergarten. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, stairways, elevator shafts, and storage areas.
[14 empty] | Education (Vocational) |  |  |  |  | Education (Vocational) | [5 empty] | Vocational School refers to buildings primarily designed to teach skilled trades to students, including trade and technical schools. Typically vocational schools are commonly post-secondary education, consisting of 1-2 years of technical/trade training. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, laboratory classrooms, stairways, elevator shafts, and storage areas.
| N/A | [12 empty] | Food (Fast Food Rest) |  |  |  |  | Food (Fast Food Rest) | [5 empty] | Fast Food Restaurant, also known as Quick Service Restaurant, refers to buildings used for the preparation and sale of ready-to-eat food. Fast Food Restaurants are characterized by a limited menu of food prepared quickly (often within a few minutes), and sometimes cooked in bulk in advance and kept hot. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, offices, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
| LEED NC - New Const'n | [12 empty] | Food (Restaurant) |  |  |  |  | Food (Restaurant) | [5 empty] | Restaurant refers to buildings used for preparation and sale of ready-to-eat food and beverages, but which do not fit in the fast food property type. Examples include fast casual, casual, and fine dining restaurants. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, offices, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
| LEED CS - Core & Shell | [12 empty] | Food Sales (specialty) |  |  |  |  | Food Sales (specialty) | [5 empty] | Food Sales refers to buildings used for the sales of food on either a retail or wholesale basis, but which do not meet the definition of Supermarket/Grocery Store, Convenience Store, or Convenience Store with Gas Stations. For example, specialty food sales like a cheese shop or butcher. Gross Floor Area should include all space within the building(s), including sales areas, storage areas, offices, kitchens, and staff break rooms.
[14 empty] | Food Service |  |  |  |  | Food Service | [5 empty] | Food Service refers to buildings used for preparation and sale of food and beverages, but which do not meet the definition of Restaurant, Cafeteria, or Bar/Nightclub. For example a bakery or coffee shop. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
[14 empty] | Gov (Convention Ctr) |  |  |  |  | Gov (Convention Ctr) | [5 empty] | Convention center refers to buildings used primarily for large conferences, exhibitions, and similar events. Convention centers may include a diverse variety of spaces, including large exhibition halls, meeting rooms, and concession stands. Gross Floor Area should include all space within the building(s), including exhibit halls, preparation and staging areas, meeting rooms, concession stands, offices, bathrooms, break rooms, security areas, elevator shafts, and stairwells. Loading dock areas located outside the walls of the building should not be included in the gross square footage.
| High Performance Energy | [12 empty] | Gov (Courthouse) |  |  |  |  | Gov (Courthouse) | [5 empty] | Courthouse refers to buildings used for federal, state, or local courts, and associated administrative office space. Gross Floor Area should include all space within the building(s), including temporary holding cells, chambers, kitchens used by staff, lobbies, atriums, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
[14 empty] | Gov (Fire Station) |  |  |  |  | Gov (Fire Station) | [5 empty] | Fire Station refers to buildings used to provide emergency response services associated with fires. Fire stations may be staffed by either volunteer or full-time paid firemen. Gross Floor Area should include all space within the building(s), including office areas, vehicle storage areas, residential areas (if applicable), storage areas, break rooms, kitchens, elevator shafts, and stairwells.
| N/A | [12 empty] | Gov (Library) |  |  |  |  | Gov (Library) | [5 empty] | Library refers to buildings used to store and manage collections of literary and artistic materials such as books, periodicals, newspapers, films, etc. that can be used for reference or lending. Gross Floor Area should include all space within the building(s), including circulation rooms, storage areas, reading/study rooms, administrative space, kitchens used by staff, lobbies, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Ground Source Heat Pump | [12 empty] | Gov (Police Station) |  |  |  |  | Gov (Police Station) | [5 empty] | Police Station applies to buildings used for federal, state, or local police forces and their associated office space. Gross Floor Area should include all space within the building(s), including offices, temporary holding cells, kitchens used by staff, lobbies, atriums, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Air Source Heat Pump | [12 empty] | Gov (Post Office) |  |  |  |  | Gov (Post Office) | [5 empty] | Mailing Center/Post Office refers to buildings used as retail establishments dedicated to mail and mailing supplies. This includes U.S. Post Offices, in addition to private retailers that offer priority mail services and mailing supplies. Gross Floor Area should include all space within the building(s), including retail counters, administrative space, kitchens used by staff, lobbies, conference rooms, storage areas, stairways, and mechanical rooms.
| Waste Heat Recovery (All types) | [12 empty] | Gov (Prison) |  |  |  |  | Gov (Prison) | [5 empty] | Prison/Incarceration refers to federal, state, local, or private-sector buildings used for the detention of persons awaiting trial or convicted of crimes. Gross Floor Area should include all space within the building(s), including holding cells, cafeterias, administrative spaces, kitchens, lobbies, atriums, conference rooms and auditoriums, fitness areas, storage areas, stairways, and elevator shafts.
[14 empty] | Hotel |  |  |  |  | Hotel | [5 empty] | Hotel refers to buildings renting overnight accommodations on a room/suite and nightly basis, and typically include a bath/shower and other facilities in guest rooms. Hotel properties typically have daily services available to guests including housekeeping/laundry and a front desk/concierge. Hotel does not apply to properties where more than 50% of the floor area is occupied by fractional ownership units such as condominiums or vacation timeshares, or to private residences that are rented out on a daily or weekly basis. Hotel properties should be majority-owned by a single entity and have rooms available on a nightly basis. Condominiums or Time Shares should select the Multifamily Housing property use. Gross Floor Area should include all interior space within the building(s), including guestrooms, halls, lobbies, atriums food preparation and restaurant space, conference and banquet space, fitness centers/spas, indoor pool areas, laundry facilities, elevator shafts, stairways, mechanical rooms, storage areas, employee break rooms, and back-of-house offices.
[14 empty] | Laboratory |  |  |  |  | Laboratory | [5 empty] | Laboratory refers to buildings that provide controlled conditions in which scientific research, measurement, and experiments are performed or practical science is taught. Gross Floor Area should include all space within the building(s) including workstations/hoods, offices, conference rooms, storage areas, decontamination rooms, mechanical rooms, elevator shafts, and stairwells.
[14 empty] | Manuf/Indust Plant |  |  |  |  | Manuf/Indust Plant | [5 empty] | Manufacturing/Industrial Plant refers to buildings used for manufacturing or assembling goods. Typically a Manufacturing/Industrial plant includes a main production area that has high-ceilings and contains heavy equipment used for assembly line production. Gross Floor Area should include all space within the building(s) at the plant, including production areas, offices, conference rooms, employee break rooms, storage areas, mechanical rooms, stairways, and elevator shafts.
[14 empty] | Medical (Amb Surg Ctr) |  |  |  |  | Medical (Amb Surg Ctr) | [5 empty] | Ambulatory Surgery Centers refers to health care facilities that provide same-day surgical care, including diagnostic and preventive procedures. Gross Floor Area should include all space within the building(s) including offices, operating and recovery rooms, waiting rooms, employee break rooms and kitchens, elevator shafts, stairways, mechanical rooms, and storage areas.
| Applicability | [12 empty] | Medical (Clinic/Emerg) |  |  |  |  | Medical (Clinic/Emerg) | [5 empty] | Urgent Care Center/Clinic/Other Outpatient Office refers to buildings used to treat patients, usually on an unscheduled, walk-in basis, who have an injury or illness that requires immediate care but is not serious enough to warrant a visit to an emergency department. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
[14 empty] | Medical (Hospital) |  |  |  |  | Medical (Hospital) | [5 empty] | Hospital refers to a general medical and surgical hospital (including critical access hospitals and children’s hospitals). These facilities provide acute care services intended to treat patients for short periods of time, including emergency medical care, physician's office services, diagnostic care, ambulatory care, surgical care, and limited specialty services such as rehabilitation and cancer care. The definition of Hospital accounts for all space types owned by the hospital that are located within the Hospital building/campus, including non-clinical spaces such as administrative offices, food service, retail, hotels, and power plant. Gross Floor Area should include all space within the building(s) on the campus including operating rooms, bedrooms, emergency treatment areas, medical offices, exam rooms, laboratories, lobbies, atriums, cafeterias, rest rooms, stairways, corridors connecting buildings, storage areas, and elevator shafts. More than 50% of the gross floor area of all buildings must be used for general medical and surgical services and more than 50% of the licensed beds must provide acute care services. Properties that use more than 50% of the gross floor area for long-term care (including long-term acute care), skilled nursing, specialty care, and/or ambulatory surgical centers or that have less than 50% of their beds licensed for acute care services are not eligible for an ENERGY STAR score. If your facility does not meet this definition, it is not eligible for an ENERGY STAR score as Hospital. You can choose from the other available healthcare property types: Ambulatory Surgical Center, Medical Office, Other/Specialty Hospital, Outpatient Rehabilitation/Physical Therapy, Urgent Care/Clinic/Other Outpatient, or Senior Care Community.
| Yes |  | Applies | [10 empty] | Medical (PT/Rehab) |  |  |  |  | Medical (PT/Rehab) | [5 empty] | Outpatient Rehabilitation/Physical Therapy offices refers to buildings used to provide diagnosis and treatment for rehabilitation and physical therapy. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, indoor pool areas, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
| No |  | N/A | [10 empty] | Medical (Vet Office) |  |  |  |  | Medical (Vet Office) | [5 empty] | A Veterinary Office refers to buildings used for the medical care and treatment of animals. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
[14 empty] | Medical Office |  |  |  |  | Medical Office | [5 empty] | Medical Office refers to buildings used to provide diagnosis and treatment for medical, dental, or psychiatric outpatient care. Gross Floor Area should include all space within the building(s) including offices, exam rooms, laboratories, lobbies, atriums, conference rooms and auditoriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
| Base Building's N/E status | [12 empty] | Office |  |  |  |  | Office | [5 empty] | Office refers to buildings used for the conduct of commercial or governmental business activities. This includes administrative and professional offices. Gross Floor Area should include all space within the building(s) including offices, conference rooms and auditoriums, kitchens used by staff, lobbies, fitness areas for staff, storage areas, stairways, and elevator shafts.
[14 empty] | Office (Financial) |  |  |  |  | Office (Financial) | [5 empty] | Financial Office refers to buildings used for financial services such as bank headquarters and securities and brokerage firms. Gross Floor Area should include all space within the building(s) including offices, trading floors, conference rooms and auditoriums, vaults, kitchens used by staff, lobbies, atriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Connected to N/E System | [12 empty] | Other |  |  |  |  | Other | [5 empty] | "Other" refers to buildings that do not fall within the available property use categories in Portfolio Manager. Before selecting Other, it is highly recommended that you review the full list of property uses available for selection to ensure that there is not a suitable category for your property. Gross Floor Area should include all space within the building(s), including space devoted to your main business activity, administrative offices, employee break rooms, bathrooms, stairways, and elevator shafts.
| Not Connected to N/E System | [12 empty] | Other (Education) |  |  |  |  | Other (Education) | [5 empty] | Other – Education refers to buildings used for religious, community, or other educational purposes not described in the available property uses in Portfolio Manager (i.e educational purposes other than adult education, college/university, K-12 school, pre-school/daycare and vocational schools). Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, auditoriums, laboratory classrooms, stairways, elevator shafts, and storage areas.
| N/A | [12 empty] | Other (Entertainment) |  |  |  |  | Other (Entertainment) | [5 empty] | Other - Entertainment/Public Assembly refers to buildings whose primary use is for entertainment or public gatherings and that do not meet the definition of any other property use defined in Portfolio Manager. Gross floor area should include all space within the building(s), including entertainment areas, administrative areas, and supporting areas such as storage rooms, hallways, restrooms, stairways, and maintenance areas.
[14 empty] | Other (Lodging/Res) |  |  |  |  | Other (Lodging/Res) | [5 empty] | Other – Lodging/Residential refers to buildings used for residential purposes other than multifamily residential, single family home, senior care community, residence hall/dormitory, barracks, prison/incarceration, or hotel. Gross Floor Area should include all space within the building(s), including living areas, common areas, administrative space, kitchens used by staff, lobbies, waiting areas, cafeterias, stairways, atriums, elevator shafts, and storage areas.
[14 empty] | Other (Mall) |  |  |  |  | Other (Mall) | [5 empty] | Other - Mall refers to buildings containing a collection of stores whose purpose is the sale of goods, but which do not fit into the enclosed mall, lifestyle center, or strip mall property types. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, storage areas, staff break rooms, walkways, stairwells, and mechanical areas.
[14 empty] | Other (Public Services) |  |  |  |  | Other (Public Services) | [5 empty] | Other – Public Services refers to buildings used by public-sector organizations to provide public services other than those described in the available property uses in Portfolio Manager (i.e. services other than offices, courthouses, drinking water treatment and distribution plants, fire stations, libraries, mailing centers or post offices, police stations, prisons or incarceration facilities, social or meeting halls, transportation terminals or stations, or wastewater treatment plants). Gross Floor Area should include all space within the building(s), including administrative space, kitchens used by staff, lobbies, waiting areas, cafeterias, stairways, atriums, elevator shafts, landscaping sheds, and storage areas.
| Neighbourhood Energy Systems | [12 empty] | Other (Recreation) |  |  |  |  | Other (Recreation) | [5 empty] | Other - Recreation refers to buildings primarily used for recreation that do not meet the definition of any other property use defined in Portfolio Manager. Gross Floor Area should include all space within the building(s), including recreational areas and supporting activities such as mechanical rooms, storage areas, elevator shafts, and stairwells.
[14 empty] | Other (Rest/Bar) |  |  |  |  | Other (Rest/Bar) | [5 empty] | Other – Restaurant/Bar refers to buildings used for preparation and sale of ready-to-eat food and beverages, but which does not fit into the fast food restaurant, restaurant, or bar/nightclub property types. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
[14 empty] | Other (Services) |  |  |  |  | Other (Services) | [5 empty] | Other - Services refers to buildings in which primarily services are offered, but which does not fit into the Personal Services or Repair Services property types. Examples include kennels, photo processing shops, etc. Gross Floor Area should include all space within the building(s), including sales floors, offices, storage areas, staff break rooms, walkways, and stairwells.
| Choose One | [12 empty] | Other (Specialty Hosp) |  |  |  |  | Other (Specialty Hosp) | [5 empty] | Other/Specialty Hospitals refers to long-term acute care hospitals, inpatient rehabilitation facilities, including Cancer Centers and Psychiatric and Substance Abuse Hospitals/Facilities. Gross Floor Area should include all space within the building(s) on the campus including: medical offices, patient rooms, laboratories, lobbies, atriums, cafeterias, rest rooms, stairways, corridors connecting buildings, storage areas, elevator shafts.
| N/A | [12 empty] | Other (Stadium) |  |  |  |  | Other (Stadium) | [5 empty] | Other - Stadium refers to buildings primarily used for sporting events that do not meet the definition of any other property use defined in Portfolio Manager. Gross Floor Area should include all space within the building(s), including areas for athletic activity and spectator seating and supporting activities such as mechanical rooms, storage areas, elevator shafts, and stairwells.
| Creative Energy (Central Heat) N/E system | [12 empty] | Other (Tech) |  |  |  |  | Other (Tech) | [5 empty] | Other – Technology/Science refers to buildings used for science and technology related services other than Laboratories and Data Centers. Gross Floor Area should include all space within the building(s), including areas with the main business activity, production areas, administrative offices, employee break areas, stairways, atriums, elevator shafts, and storage areas.
| City Owned False Creek NEU Service Area | [12 empty] | Other (Utility) |  |  |  |  | Other (Utility) | [5 empty] | Other – Utility applies to buildings used by a utility for some purpose other than general office or energy/power generation. This may include utility transfer stations or maintenance facilities. Note that an administrative office occupied by a utility should be entered as Office, and a power or energy generation plant should be entered as Energy/Power Station. Gross Floor Area should include all space within the building(s), including administrative space, maintenance and equipment areas, generator rooms, kitchens used by staff, lobbies, meeting rooms, stairways, elevator shafts, and storage areas. This should not include any exterior spaces associated with utility operations.
| East Fraserlands (River District) N/E system | [12 empty] | Parking |  |  |  |  | Parking | [5 empty] | Parking refers to buildings and lots used for parking vehicles. This includes open parking lots, parking structures that may be only partially enclosed, and fully-enclosed (or underground) parking structures. Parking structures may be free standing or may be physically connected to another building.
| Oakridge Energy D/E system | [12 empty] | Personal Services |  |  |  |  | Personal Services | [5 empty] | Personal Services refers to buildings used to sell services rather than physical goods. Examples include dry cleaners, salons, spas, etc. Gross Floor Area should include all space within the building(s), including sales floors, offices, storage areas, staff break rooms, walkways, and stairwells.
| Total site of 8,000 m2 or greater | [12 empty] | Rec (Aquarium) |  |  |  |  | Rec (Aquarium) | [5 empty] | Aquarium refers to buildings used to provide aquatic habitat primarily to live animals and which may include public or private viewing areas and educational programs. Gross Floor area should include public and restricted areas such as visitor walkways, tank space, retail areas, restaurants, laboratories, classrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Areas not in enclosed buildings, such as outdoor habitats, open-air theaters, walkways, and landscaped areas should not be included in the Gross Floor Area.
| Total new development of 45,000 m2 or greater | [12 empty] | Rec (Arena - indoor) |  |  |  |  | Rec (Arena - indoor) | [5 empty] | Indoor Arena refers to enclosed structures used for professional or collegiate sports and entertainment events. Examples of events held in indoor arenas include basketball and hockey games, circus performances, and concerts. Indoor Arenas usually have capacities of 5,000 seats or more and are often characterized by multiple concourses and concession areas.
[14 empty] | Rec (Bar/Nightclub) |  |  |  |  | Rec (Bar/Nightclub) | [5 empty] | Bar/Nightclub refers to buildings used primarily for social/entertainment purposes, and is characterized by most of the revenue being generated from the sale of beverages instead of food. Gross Floor Area should include all space within the building(s), including standing/seating areas, stage/dressing room areas, food/drink preparation or kitchen areas, retail areas, bathrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Properties whose primary business revenues are generated from the sale of food should be entered using one of the Restaurant property uses, even if there is a bar.
[14 empty] | Rec (Bowling Alley) |  |  |  |  | Rec (Bowling Alley) | [5 empty] | Bowling alley refers to buildings used for public or private, recreational or professional bowling. Gross Floor Area should include all space within the building(s), including bowling lanes, concession areas, party rooms, retail areas, administrative/office space, employee break rooms, storage areas, and mechanical rooms.
[14 empty] | Rec (Casino) |  |  |  |  | Rec (Casino) | [5 empty] | Casino refers to buildings primarily used to conduct gambling activities including both electronic and live table games. Gross Floor Area should include all space within the building(s), including the main casino floor/gaming area, restaurants/bars, retail areas, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. If your Casino is located in the same building as a hotel, we recommend that you enter a separate hotel property use.
[14 empty] | Rec (Fitness Ctr/Gym) |  |  |  |  | Rec (Fitness Ctr/Gym) | [5 empty] | Fitness Center/Health Club/Gym refers to buildings used for recreational or professional athletic training and related activities. Gross Floor Area should include all space within the building(s), including weight and cardio equipment areas, personal training areas, courts, locker rooms, sauna and spa areas, retail areas, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
[14 empty] | Rec (Ice/Curling Rink) |  |  |  |  | Rec (Ice/Curling Rink) | [5 empty] | Ice/Curling Rink refers to buildings that include one or more ice sheets used for public or private, recreational or professional skating, curling, hockey, or other similar activities. Gross Floor Area should include all space within the building(s), including ice area, spectator areas, concession stands, retail areas, locker rooms, administrative/office areas, employee break rooms, mechanical rooms, and storage areas. Larger facilities primarily serving professional or collegiate functions and with significant spectator seating should review the definition for Indoor Arena to determine the best classification.
[14 empty] | Rec (Movie Theatre) |  |  |  |  | Rec (Movie Theatre) | [5 empty] | Movie theater refers to buildings used for public or private film screenings. Gross Floor Area should include all space within the building(s), including seating areas, lobbies, concession stands, bathrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
| Renewable & HP Energies | [12 empty] | Rec (Museum) |  |  |  |  | Rec (Museum) | [5 empty] | Museum refers to buildings that display collections to outside visitors for public viewing and enjoyment and for informational/educational purposes. Gross Floor Area should include all space within the building(s), including public collection display areas, meeting rooms, classrooms, gift shops, food service areas, administrative/office space, mechanical rooms, storage areas for collections, elevator shafts, and stairwells.
[14 empty] | Rec (Performing Arts) |  |  |  |  | Rec (Performing Arts) | [5 empty] | Performing Arts refers to buildings used for public or private artistic or musical performances. Gross Floor Area should include all space within the building(s), including seating, stage and backstage areas, food service areas, retail areas, rehearsal studios, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
| Photovoltaic systems | [12 empty] | Rec (Race Track) |  |  |  |  | Rec (Race Track) | [5 empty] | Race Track refers to buildings used primarily to hold racing events such as vehicle races, track/field races, horse races, and/or dog-races. Gross Floor Area should include all spectator viewing areas, concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the race track itself should also be included in the gross floor area, along with the footprint of any staging areas.
| Solar Thermal systems | [12 empty] | Rec (Roller Rink) |  |  |  |  | Rec (Roller Rink) | [5 empty] | Roller Rink refers to buildings used primarily for roller-skating, inline skating/rollerblading, or skateboarding. Gross Floor Area should include all space within the building(s), including the rink space, concession areas, locker rooms, retail areas, administrative/office areas, employee break rooms, mechanical rooms, and storage areas.
| Bio-fuel based energy | [12 empty] | Rec (Social/Mtg Hall) |  |  |  |  | Rec (Social/Mtg Hall) | [5 empty] | Social/Meeting hall refers to buildings primarily used for public or private gatherings. This may include community group meetings, seminars, workshops, or performances. Please note that there is another property use available, Convention Center, for large exhibition and conference facilities. Gross Floor Area should include all space within the building(s), including meeting rooms, auditoriums, food service areas, lobbies, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
| Geothermal Heating | [12 empty] | Rec (Stadium - closed) |  |  |  |  | Rec (Stadium - closed) | [5 empty] | Stadium (Closed) refers to structures with a permanent or retractable roof which are used primarily for professional or collegiate sports and entertainment events. Examples of events held in closed stadiums include baseball and football games, and concerts. Closed Stadiums usually have capacities of 25,000 seats or more and are often characterized by multiple concourses and concession areas. Gross Floor Area should include all space within the building(s), including concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the playing field should also be included in the gross floor area.
| Geothermal Electric | [12 empty] | Rec (Stadium - open) |  |  |  |  | Rec (Stadium - open) | [5 empty] | Stadium (Open) refers to structures used primarily for professional or collegiate sports and entertainment events in which the playing field is not covered and is exposed to the outside. Examples of events held in open stadiums include baseball, football, and soccer games, and concerts. Open Stadiums usually have capacities of 5,000 seats or more and are often characterized by multiple concourses and concession areas. Gross Floor Area should include all space within the building(s), including concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the playing field should also be included in the gross floor area.
| Ground Source Heat Pump | [12 empty] | Rec (Swimming Pool) |  |  |  |  | Rec (Swimming Pool) | [5 empty] | Swimming Pool refers to any heated swimming pools located either inside or outside. To enter a swimming pool, a specific pool size must be selected. In order to enter buildings associated with a Swimming Pool, the main property use must be entered (e.g., K-12 School, Hotel, Fitness Center/Health Club/Gym, etc).
| Air Source Heat Pump | [12 empty] | Rec (Zoo) |  |  |  |  | Rec (Zoo) | [5 empty] | Zoo refers to buildings used primarily to provide habitat to live animals and which may include public or private viewing and educational programs. Gross Floor Area should include all space within all fully enclosed buildings, including, habitats, visitor viewing areas, theaters, classrooms, food service areas, retail stores, veterinary offices, exhibit space, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Areas not in fully enclosed buildings, such as outdoor habitats, open-air theaters, walkways, and landscaped areas should not be included in the Gross Floor Area.
| Waste Heat Recovery (All types) | [12 empty] | Residential (Barracks) |  |  |  |  | Residential (Barracks) | [5 empty] | Barracks refers to residential buildings associated with military facilities or educational institutions which offer multiple accommodations for long-term residents. Gross Floor Area should include all space within the building(s), including bedrooms, common areas, food service facilities, laundry facilities, meeting spaces, exercise rooms, health club/spas, lobbies, elevator shafts, storage areas, and stairways.
[14 empty] | Residential (Hall/Dorm) |  |  |  |  | Residential (Hall/Dorm) | [5 empty] | Residence Hall/Dormitory refers to buildings associated with educational institutions or military facilities which offer multiple accommodations for long-term residents. Gross Floor Area should include all space within the building(s), including bedrooms, common areas, food service facilities, laundry facilities, meeting spaces, exercise rooms, health club/spas, lobbies, elevator shafts, storage areas, and stairways.
[14 empty] | Res (Multifamily-Common Areas) |  |  |  |  | Res (Multifamily-Common Areas) | [5 empty] | Multifamily-Common Areas refers only to the common areas of residential buildings that contain more than two residential living units. These properties may be high rise buildings (4 or more stories), or mixed use buildings of 3 stories or less. Occupants of these buildings may include tenants, cooperators, and/or individual owners. IMPORTANT: Work done on the building's envelope is considered base building work and should use this checklist. For work done within residential suites, applicants are to use the Alterations to Residential Suites checklist.
[14 empty] | Residential (Senior Care) |  |  |  |  | Residential (Senior Care) | [5 empty] | Senior Care Community refers to buildings that house and provide care and assistance for elderly residents. Gross Floor Area should include all space within the building(s) including individual rooms or units, wellness centers, exam rooms, community rooms, small shops or service areas for residents and visitors (e.g. hair salons, convenience stores), staff offices, lobbies, atriums, cafeterias, kitchens, storage areas, hallways, basements, stairways, corridors between buildings, and elevator shafts. The ENERGY STAR score for Senior Care community applies to nursing homes (skilled nursing facilities) and assisted living facilities. Independent senior living communities are not eligible. However, it is common for some Senior Care Communities to offer a mix of residential options including independent living, assisted living, and skilled nursing. More than 50% of the units in a community must be considered skilled nursing and/or assisted living in order to be eligible for an ENERGY STAR score as a Senior Care Facility. One exception to this rule is for communities in which 50% or more of the units are independent living (IL) but the IL buildings are separately metered stand-alone buildings, a valid rating can be generated only by fully excluding the IL buildings from the rest of the campus. Facilities with more than 50% independent living units cannot earn an ENERGY STAR score and should benchmark using the Multifamily property type.
[14 empty] | Retail |  |  |  |  | Retail | [5 empty] | Retail Store refers to individual stores used to conduct the retail sale of non-food consumer goods such as clothing, books, toys, sporting goods, office supplies, hardware, and electronics. Buildings containing multiple stores should be classified as enclosed mall, lifestyle center, or strip mall. Gross Floor Area should include all space within the building(s), including sales areas, storage areas, offices staff break rooms, elevators, and stairwells. To receive an ENERGY STAR score, a Retail Store must be asingle store that is at least 5,000 square feet and has an exterior entrance to the public. The ENERGY STAR score applies to: Department Stores, Discount Stores, Supercenters, Warehouse Clubs, Drug Stores, Dollar Stores, Home Center/Hardware Stores, and Apparel/Specialty Stores (e.g. books, clothing, office products, toys, home goods, and electronics). Eligible store configurations include: free standing stores; stores located in open air or strip centers (a collection of attached stores with common areas that are not enclosed); and mall anchors. Retail configurations not eligible to receive an ENERGY STAR score include: enclosed malls; individual stores located within enclosed malls; lifestyle centers; strip malls; and individual stores that are part of a larger non- mall building (i.e. office or hotel). Convenience Stores, Automobile Dealerships, and Restaurants are not eligible to earn an ENERGY STAR score as Retail. Supermarkets are eligible for an ENERGY STAR score under the Supermarket property type. Note: In order to be eligible to earn ENERGY STAR certification, your building must be located in the US or its territories, or owned by the US government outside of the US.
[14 empty] | Retail (Auto Dealership) |  |  |  |  | Retail (Auto Dealership) | [5 empty] | Automobile Dealership refers to buildings used for the sale of new or used cars and light trucks. Gross Floor Area should include all space within the building(s), including sales floors, offices, conference rooms, vehicle service centers, parts storage areas, waiting rooms, staff break rooms, hallways, and stairwells. Gross Floor Area should not include any exterior spaces such as vehicle parking areas.
[14 empty] | Retail (Conv w Gas Stn) |  |  |  |  | Retail (Conv w Gas Stn) | [5 empty] | Convenience Store with Gas Station refers to buildings that are co-located with gas stations and are used for the sale of a limited range of items such as groceries, toiletries, newspapers, soft drinks, tobacco products, and other everyday items. Convenience Store with Gas Station may include space for vehicle servicing and repair. Gross Floor Area should include all space within the building(s), including sales floors, offices, staff break rooms, storage areas, and vehicle repair areas. Energy use associated with outside areas such as vehicle parking and gas filling areas should be included with the total energy use for the building(s), but the square footage associated with these outdoor areas should not be included in the Gross Floor Area.
[14 empty] | Retail (Convenience St) |  |  |  |  | Retail (Convenience St) | [5 empty] | Convenience Store without Gas Station refers to buildings used for the sale of a limited range of items such as groceries, toiletries, newspapers, soft drinks, tobacco products, and other everyday items, which are not co-located with a gas station. Gross Floor Area should include all space within the building(s), including sales floors, offices, staff break rooms, and storage areas. Conference facilities located within a Hotel should be included along with your Hotel property use details, rather than added as a separate Convention Center property use. Conference facilities primarily serving smaller meetings should be entered as Social/Meeting Hall.
[14 empty] | Retail (Lifestyle Ctr) |  |  |  |  | Retail (Lifestyle Ctr) | [5 empty] | Lifestyle Center refers to a mixed use commercial development that includes retail stores and leisure amenities, where individual retail stores typically contain an entrance accessible from the outside and are not connected by internal walkways. Lifestyle centers have an open air design, unlike traditional enclosed malls, and often include landscaped pedestrian areas, as well as streets and vehicle parking. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, residential areas, storage areas, staff break rooms, walkways, stairwells, and mechanical areas. Do not include any exterior spaces such as pedestrian walkways or vehicle parking areas.
[14 empty] | Retail (Mall - enclosed) |  |  |  |  | Retail (Mall - enclosed) | [5 empty] | Enclosed Mall refers to buildings that house multiple stores, often “anchored” by one or more department stores, and with interior walkways. Most stores will not have entrances accessible from outside, with the exception of the “anchor” stores. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, storage areas, staff break rooms, atriums, walkways, stairwells, and mechanical rooms.
[14 empty] | Retail (Repair: Car/Shoe) |  |  |  |  | Retail (Repair: Car/Shoe) | [5 empty] | Repair Services refers to buildings in which some type of repair service is provided. Examples include vehicle service or repair shops, shoe repair, jewelry repair, locksmiths, etc. Gross Floor Area should include all space within the building(s), including sales floors, repair areas, workshops, offices, parts storage areas, waiting rooms, staff break rooms, hallways, and stairwells.
[14 empty] | Retail (Strip Mall) |  |  |  |  | Retail (Strip Mall) | [5 empty] | Strip mall refers to buildings comprising more than one retail store, restaurant, or other business, in an open-air configuration where each establishment has an exterior entrance to the public and there are no internal walkways. Gross Floor Area should include all space within the building(s), including retail stores, offices, restaurants, storage areas, staff break rooms, and stairwells. Do not include any exterior spaces such as vehicle parking areas. Note that individual stores within strip malls may be eligible to receive an ENERGY STAR score if they are over 5,000 square feet in size and have an exterior entrance to the public.
[14 empty] | Retail (Supermkt/Groc) |  |  |  |  | Retail (Supermkt/Groc) | [5 empty] | Supermarket/Grocery Store refers to buildings used for the retail sale of primarily food and beverage products, and which may include small amounts of preparation and sale of ready-to-eat food. Buildings where the primary business is the on-site preparation and sale of ready-to-eat food should use one of the Restaurant property types. Gross Floor Area should include all space within the building(s), including the sales floor, offices, storage areas, kitchens, staff break rooms, and stairwells. Gross Floor Area should include all space within the building, including court/rink space, all concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells.
[14 empty] | Retail (Wholesale Club) |  |  |  |  | Retail (Wholesale Club) | [5 empty] | Wholesale Club/Supercenter refers to buildings used to conduct the retail sale of a wide variety of merchandise, typically in bulk quantities. Merchandise may include food, clothing, office supplies, furniture, electronics, books, sporting goods, toys, and hardware. Gross Floor Area should include all space within the building(s), including the sales floor, offices, storage areas, kitchens, staff break rooms, elevators, and stairwells.
[14 empty] | Self Storage Facility |  |  |  |  | Self Storage Facility | [5 empty] | Self-Storage Facility refers to buildings that are used for private storage. Typically, a single Self Storage Facility will contain a variety of individual units that are rented out for the purpose of storing personal belongings. Gross Floor Area should include all space within the building(s), including individual storage units, administrative offices, security and maintenance areas, mechanical rooms, hallways, stairways, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[14 empty] | Trans Terminal/Station |  |  |  |  | Trans Terminal/Station | [5 empty] | Transportation Terminal/Station applies to buildings used primarily for accessing public or private transportation. This includes train stations, bus stations, airports, and seaports. These terminals include areas for ticket purchases, and embarkation/disembarkation, and may also include public waiting areas with restaurants and other concessions. Gross Floor Area should include all space within the building(s), including boarding areas, waiting areas, administrative space, kitchens used by staff, lobbies, restaurants, cafeterias, stairways, atria, elevator shafts, and storage areas. This should not includeany exterior spaces associated with the terminals, such as drop-off areas, outdoor platforms, or outdoor loading docks/bays.
[14 empty] | Unknown (Core & Shell) |  |  |  |  | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
[14 empty] | Warehouse (Non-Refrig) |  |  |  |  | Warehouse (Non-Refrig) | [5 empty] | Non-Refrigerated Warehouse refers to unrefrigerated buildings that are used to store goods, manufactured products, merchandise or raw materials. Gross Floor Area should include all space within the building(s), including the main storage rooms, administrative office offices, lobbies, stairways, restrooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[14 empty] | Warehouse (Refrig) |  |  |  |  | Warehouse (Refrig) | [5 empty] | Refrigerated Warehouse refers to refrigerated buildings that are used to store perishable goods or merchandise under refrigeration at temperatures below 50 degrees Fahrenheit. Gross Floor Area should include all space within the building(s), which includes temperature-controlled areas, administrative offices, lobbies, stairways, restrooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[14 empty] | Worship Facility |  |  |  |  | Worship Facility | [5 empty] | Worship Facility refers to buildings that are used as places of worship. This includes churches, temples, mosques, synagogues, meetinghouses, or any other buildings that primarily function as a place of religious worship. Gross Floor Area should include all areas inside the building that includes the primary worship area, including food preparation, community rooms, classrooms, and supporting areas such as restrooms, storage areas, hallways, and elevator shafts. The ENERGY STAR score for Worship Facilities applies to buildings that function as the primary place of worship and not to other buildings that may be associated with a religious organization, such as living quarters, schools, or buildings used primarily for other community activities. To receive an ENERGY STAR score, a Worship facility must have at least 25 seats, but cannot have more than 4,000.
[14 empty] | Unknown (Core & Shell) |  |  |  |  | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
NECB Section
| NECB Section | [10 empty] | Entire Energy Package (checklist + all supporting docs)
| Admin | [10 empty] | Admin - Checklist
| Building Envelope | [10 empty] | Building Envelope Compliance
| Lighting | [10 empty] | Lighting Compliance
| HVAC | [10 empty] | HVAC Compliance
| Service Water Heating | [10 empty] | Service Water Heating Compliance
Note on B3: Insert the building's main address on this line. If your space is within the main building then also indicate the unit or suite number if any. For buildings with multiple commercial spaces, each having unique addresses, insert the building's main address here then the specific commercial space's address on the next row below.
Note on B4: If your space is a retail or commercial unit within a building, and your space has a different address from the main building, then put the building's address on the row above and the address of the retail or commercial unit on this row, starting with a unit number if any.
Note on C13: Most spaces have only one use. If more than one use then indicate all space uses. If more than one space or tenancy, then indicate uses, if more than one. Example: If a single tenancy (office) is becoming two tenancies (Retail, and Medical Office) then indicate based on size, with Primary being largest tenancy.
Note on C25: Do not include the City neighbourhood energy systems here. See below for declaration of City neighbourhood energy systems.
Note on D39: If building a complete wall or a complete roof, then comply with NECB 2015 envelope requirements and use envelope forms provided in the Building Envelpe tab. If only doing partial work or cladding work etc then submit only the Calculator to show that the envelope performance has not been made worse.
Note on D69: Choose the necessary area of revision (Env, Lighting, HVAC, SWH) here, then the associated revised document for resubmission, on the same row, in the column to the right.
Note on H3: Insert the suite or unit number if your space uses the address of the main building, otherwise leave blank.
Note on H4: Insert the suite number, if any, of your commercial space, otherwise leave blank.
Note on H13: Indicate Usage(s) starting with largest area, then add in order of decreasing area.
Note on H16: Use this cell to see a detailed description of the building(s) being considered above. To see the description, first choose the building from the drop box in this cell. The detailed description of the selected building will appear outside the checklist, to the right.
Note on I20: If not applicable, indicate "N/A". Indicate EUI requirement per the Rezoning Conditions.
Note on I21: If not applicable, indicate "N/A". Indicate EUI achieved per the modeling output (ECB).
Note on J28: If the existing building is already tied into an N/E system then choose the "Connected…" option. If within an N/E area but the building is not connected to the N/E system then choose the "Not Connected…" option. If the building is not within an N/E area then choose the "N/A" option.
Note on K3: Insert Building number.
Note on K4: Insert Tenancy number.
Note on N35: Answer "Yes" if your scope of work on the building envelope includes the addition, deletion or replacement of glazing, skylights, doors, or insulation. If you are only refurbishing then reinstalling the original components then answer "No".
Note on N41: If you are adding lighting load, answer "Yes". If you are altering luminaires (replacing, removing, or relocating from one space into another) then answer "Yes", otherwise answer "No".
Note on N47: If you are adding any HVAC equipment (including kitchen exhaust and make-up air systems) that has an energy component such as motors ( >1 hp ), burners, coils, or heat exchangers, then answer "Yes". If you are only repairing existing equipment or moving diffuser locations then answer "No".
Note on N55: If you are adding any Service Water Heating equipment (boilers, hot water heater, on-demand system) that has an energy component such as motors, burners, coils, or heat exchangers, then answer "Yes". If you are only repairing or relocating existing equipment, then answer "No".
Note on O3: Insert building's street name by using drop box.
Note on O4: Insert tenancy's street name by using drop box.
Note on O13: Indicate area in square meters. Example: 3540 not 3540sqm.
Note on P35: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P41: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P47: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P55: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on Q20: Input to first decimal, without % sign. Example: 20.0 Indicate the required energy cost savings (reduction) beyond 90.1-2010, as stipulated by the Rezoning Conditions. Note: Savings to be measured in % energy cost saved.
Note on Q21: Input to first decimal, without % sign. Example: 20.0 This cell indicates the energy cost improvement (reduction) achieved beyond 90.1-2010, by percentage. Note, this measures energy cost savings, not energy savings.
Note on S59: Indicate "X" if you are providing a water heating system that satisfies the requirements. Indicate "N/A" if a water heating system is not provided.
Note on T21: New Construction or Core & Shell
Note on Y51: Insert source of input per these examples: - ASHRAE 62 - 2001 (except Addendum n) or - ASHRAE 62.1 - 20__ etc
Note on Y53: Insert source of input per these examples: - Actual: Supplied by Owner or - ASHRAE 90.1 - 20__ Table or Chart # etc
Note on AB25: Indicate here any additional High Performance Energy system not listed within Drop-Down menu.
Note on AD24: Indicate here any additional Renewable Energy system not listed within Drop-Down menu.
Note on AE3: Submit without number, then update once permit number is known.
Note on AE20: Indicate level of LEED Certification required by Rezoning Conditions.
Note on AE21: Indicate level of LEED Certification achieved.
Note on AF13: Intent: Account for all conditioned non-Residential (commercial etc) spaces only. If area is zero or Not Applicable then input 0, not N/A or 0sqm. Space Area calculation: Calculate all areas except "non-conditioned" spaces. This means to exclude all outside spaces (patios), and include all interior spaces (ie storage, etc) as long as they are conditioned.
Note on AF14: If area is zero or Not Applicable then input 0, not N/A or 0 sqm. Intent: i) If scope includes Building Envelope work of a residential unit, use area of conditioned Residential space(s) only. ii) ASHRAE does not apply to areas within residential suites, just the common areas of residential buildings (and envelope per i above), therefore, indicate total area of common spaces being worked on. "Conditioned" Space Area calculation: Calculate all areas except "non-conditioned" spaces. This means to exclude all outside spaces (patios), and include all interior spaces (ie storage, etc) as long as they are conditioned.
Note on AF15: Intent: Account for all semiheated spaces only. If area is zero or Not Applicable then input 0, not N/A or 0sqm.
Note on AG16: Answer "Yes" if the entrance to the space is directly from the outdoors. Answer "No" if the entrance to the space is via another interior space such as a corridor or mall.
Note on AG17: Answer N/A if there is no outdoor entrance. Answer "Yes" if a new entrance is being built for the space, or if the existing outdoor entrance to the space is being modified. Answer "No" if the existing outdoor entrance to the space is not being modified.
Note on AG20: Indicate number of LEED energy pts (EAc1) required by Rezoning Conditions. If not specified, indicate N/A but still indicate number of pts achieved below.
Note on AG21: Indicate number of LEED energy pts (EAc1) achieved as shown on LEED Letter Template for EAc1.
Note on AG31: Are either architects or engineers involved in this project?
Note on AG33: Only Food and/or Beverage establishments are eligible for exterior patio heating systems.

## Sample Checklist - First TI
Energy Checklist for First TIs within NECB/ZEBP Buildings
Building Use description will appear here.
Building Address : | [5 empty] | 1201 |  |  | 525 |  |  |  | ABERDEEN STREET | [8 empty] | Building Permit Application No.: |  |  |  | BP-2025-12345
Tenancy Address :
This form is to be completed digitally. For ease of use, drop boxes and pop-up instructions are included.
IMPORTANT - Submission Format and Process:
Effective September 15, 2025, this First TI checklist is to be completed and submitted at the Building Permit application stage. Submit online with your Building Permit application. Include all relevent documents pertaining to scope of work.
Space Use, Area & Performance Information
| Primary Use/Area: |  |  |  |  | Office | [6 empty] | 4250 |  | 73.91% |  | TI Space(s) | Non-residential Cond'd Space Area (m2): | [8 empty] | 425
| Second Use/Area: |  |  |  |  | Retail | [6 empty] | 1500 |  | 26.09% |  |  | Resid Cond'd Common Space Area (m2): | [8 empty] | 0
| Tertiary Use/Area: | [16 empty] | Semiheated Space Area (m2): | [8 empty] | 0
| Total Area (m2): |  |  |  |  | Building Use Description | [6 empty] | 5750 |  |  |  |  | Is public access via an outdoor entrance? | [9 empty] | No
[18 empty] | Is existing outdoor entrance being modified? | [9 empty] | No
Neighbourhood Energy (N/E) Systems
| Rz Cond's |  | EUI required: | [5 empty] | Energy reduction: | [6 empty] | LEED ver: | [5 empty] | LEED targets:
|  |  | achieved: | [6 empty] | achieved: | [12 empty] | achieved:
Renewable / High Performance Energy Systems
- Renewable Energy systems:
- High Performance Energy systems:
| If within a Neighbourhood Energy area, indicate which system: | [17 empty] | N/A
| Base Building's N/E status: | [6 empty] | N/A | [14 empty] | TI's thermal energy requirement: | N/A
| VBBL (10.2.1.2/10.2.1.3) - Deliverables for NECB/ZEBP First TIs | [25 empty] | Are Reg'd Professionals involved with this project? | No
[27 empty] | 10.2.2.19. - Does the proposed scope of work include the design and provision of exterior patio/space heating systems? | No
| NECB Part 3) Building Envelope | [10 empty] | No |  | Owner - J Smith | [12 empty] | Applicability: | N/A
|  | N/A |  | Building Envelope Compliance Table (tab below) | [11 empty] | N/A |  | Energy Statements on Drawings | [8 empty] | Dwg #: | N/A
| or; | N/A |  | Building Envelope Energy Perf Comparison Calc | [11 empty] | N/A |  | Complies with NECB Envelope Alterations (2.1.1)
| NECB Part 4) Lighting | [10 empty] | Yes |  | DEF Electrical - R. Johnson | [12 empty] | Applicability: | Applies
|  | X |  | Lighting Compliance Table (tab below) | [11 empty] | X |  | Energy Statements on Drawings | [8 empty] | Dwg #: | E-1
[16 empty] | X |  | Drawing: Reflected Ceiling Plan | [8 empty] | Dwg #: | E-4
| NECB Part 5) HVAC | [10 empty] | Yes |  | ABC Mechanical - S. Jones | [12 empty] | Applicability: | Applies
|  | X |  | HVAC Compliance Table (tab below) | [11 empty] | X |  | Energy Statements on Drawings | [8 empty] | Dwg #:
[20 empty] | Source of Ventilation design: | ASHRAE 62-2001 (except addendum n)
[20 empty] | Source of Operation Schedule: | Actual: Supplied by Owner/Tenant
| NECB Part 6) Service Water Htg | [10 empty] | No |  | ABC Mechanical - S. Jones | [12 empty] | Applicability: | N/A
|  | N/A |  | Service Water Htg Compliance Table (tab below) | [11 empty] | N/A |  | Energy Statements on Drawings | [8 empty] | Dwg #: | N/A
[16 empty] | N/A |  | Electric/Gas Water Heating System is Allowed
OCCUPANCY PERMIT STAGE
| Check one only; | [5 empty] | Building Permit stage submission is complete and accurate - No Revisions Required | [8 empty] | OR |  | Submitting revised Deliverables (Submit only the documentation that differs from Building Permit stage Deliverables)
List All Revised and Resubmitted Deliverables Using Drop-Down Boxes Below;
|  | NECB Part | [8 empty] | Revised Documentation
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [20 empty] | DOC/2012/155502 |  |  |  | Version: |  | 250425-1
Drop Down Boxes
| Box 1 |  |  | Box 2 |  |  | Renewable Energy | [6 empty] | Box 4 | [8 empty] | Box 6 |  | N/E | [5 empty] | Box 8
| Yes |  |  | Yes |  |  | N/A | [6 empty] | X | [8 empty] | Yes |  | Use Base Building N/E System | [5 empty] | X
| No |  |  | No |  |  | Photovoltaic systems | [6 empty] | N/A | [8 empty] | N/A |  | None
|  |  |  | N/A |  |  | Solar Thermal systems | [17 empty] | N/A
Bio-fuel based energy
Geothermal Heating
Geothermal Electric
Low-impact Hydro Electric
Wave & Tidal Power
| LEED Version | [6 empty] | LEED Certif | [7 empty] | Building Use(s) | [6 empty] | Building Use(s)
| N/A | [21 empty] | Building Use Description | [5 empty] | Building Use description will appear here.
| LEED v1.0 | [6 empty] | N/A | [7 empty] | Unknown (Core & Shell) | [6 empty] | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
| LEED v1.1 | [6 empty] | Platinum | [7 empty] | Bank Branch | [6 empty] | Bank Branch | [5 empty] | Bank Branch refers to a commercial banking outlet that offers banking services to walk-in customers. Gross Floor Area should include all space within the building(s), including banking areas, vaults, lobbies, atriums, kitchens used by staff, conference rooms, storage areas, stairways, and elevator shafts.
| LEED 2009 | [6 empty] | Gold | [7 empty] | Data Centre | [6 empty] | Data Centre | [5 empty] | Data Center refers to buildings specifically designed and equipped to meet the needs of high density computing equipment, such as server racks, used for data storage and processing. Typically these facilities require dedicated uninterruptible power supplies and cooling systems. Data center functions may include traditional enterprise services, on-demand enterprise services, high performance computing, internet facilities, and/or hosting facilities. Often Data Centers are free standing, mission critical computing centers. When a data center is located within a larger building, it will usually have its own power and cooling systems, and require a constant power load of 75 kW or more. Data Center is intended for sophisticated computing and server functions; it should not be used to represent a server closet or computer training area. Gross Floor Area should include all space within the building(s) including raised floor computing space, server rack aisles, storage silos, control console areas, battery rooms, mechanical rooms for cooling equipment, administrative office areas, elevator shafts, stairways, break rooms and restrooms.
| LEED Mid Rise | [6 empty] | Silver | [7 empty] | Distribution Centre | [6 empty] | Distribution Centre | [5 empty] | Distribution Center refers to unrefrigerated buildings that are used for the temporary storage and redistribution of goods, manufactured products, merchandise or raw materials. Gross Floor Area should include all space within the building(s) including space designed to store non-perishable goods and merchandise, offices, lobbies, stairways, rest rooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
| LEED v4 | [6 empty] | Certified | [7 empty] | Education (Adult C Educ) | [6 empty] | Education (Adult C Educ) | [5 empty] | Adult Education refers to buildings used primarily for providing adult students with continuing education, workforce development, or professional development outside of the college or university setting. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, auditoriums, stairways, atriums, elevator shafts, and storage areas.
[16 empty] | Education (College/Univ) | [6 empty] | Education (College/Univ) | [5 empty] | College/University refers to buildings used for the purpose of higher education. This includes public and private colleges and universities. Gross Floor Area should include all space within the building(s), including classrooms, laboratories, offices, cafeterias, maintenance facilities, arts facilities, athletic facilities, residential areas, storage rooms, restrooms, elevator shafts, and stairways.
[16 empty] | Education (K-12) | [6 empty] | Education (K-12) | [5 empty] | K-12 School refers to buildings or campuses used as a school for Kindergarten through 12th grade students. This does not include college or university classroom facilities/laboratories, or vocational, technical, trade, adult, or continuing education schools. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, laboratory classrooms, portable classrooms, greenhouses, stairways, atriums, elevator shafts, small landscaping sheds, and storage areas. The ENERGY STAR score for K-12 School does not apply to preschool or day care buildings; in order to classify as K-12 school, more than 75% of the students must be in kindergarten or older.
| LEED Type | [14 empty] | Education (Pre/Daycare) | [6 empty] | Education (Pre/Daycare) | [5 empty] | Pre-school/Daycare applies to buildings used for educational programs or daytime supervision/recreation for young children before they attend Kindergarten. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, stairways, elevator shafts, and storage areas.
[16 empty] | Education (Vocational) | [6 empty] | Education (Vocational) | [5 empty] | Vocational School refers to buildings primarily designed to teach skilled trades to students, including trade and technical schools. Typically vocational schools are commonly post-secondary education, consisting of 1-2 years of technical/trade training. Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, gymnasiums, auditoriums, laboratory classrooms, stairways, elevator shafts, and storage areas.
| N/A | [14 empty] | Food (Fast Food Rest) | [6 empty] | Food (Fast Food Rest) | [5 empty] | Fast Food Restaurant, also known as Quick Service Restaurant, refers to buildings used for the preparation and sale of ready-to-eat food. Fast Food Restaurants are characterized by a limited menu of food prepared quickly (often within a few minutes), and sometimes cooked in bulk in advance and kept hot. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, offices, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
| LEED NC - New Const'n | [14 empty] | Food (Restaurant) | [6 empty] | Food (Restaurant) | [5 empty] | Restaurant refers to buildings used for preparation and sale of ready-to-eat food and beverages, but which do not fit in the fast food property type. Examples include fast casual, casual, and fine dining restaurants. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, offices, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
| LEED CS - Core & Shell | [14 empty] | Food Sales (specialty) | [6 empty] | Food Sales (specialty) | [5 empty] | Food Sales refers to buildings used for the sales of food on either a retail or wholesale basis, but which do not meet the definition of Supermarket/Grocery Store, Convenience Store, or Convenience Store with Gas Stations. For example, specialty food sales like a cheese shop or butcher. Gross Floor Area should include all space within the building(s), including sales areas, storage areas, offices, kitchens, and staff break rooms.
[16 empty] | Food Service | [6 empty] | Food Service | [5 empty] | Food Service refers to buildings used for preparation and sale of food and beverages, but which do not meet the definition of Restaurant, Cafeteria, or Bar/Nightclub. For example a bakery or coffee shop. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
[16 empty] | Gov (Convention Ctr) | [6 empty] | Gov (Convention Ctr) | [5 empty] | Convention center refers to buildings used primarily for large conferences, exhibitions, and similar events. Convention centers may include a diverse variety of spaces, including large exhibition halls, meeting rooms, and concession stands. Gross Floor Area should include all space within the building(s), including exhibit halls, preparation and staging areas, meeting rooms, concession stands, offices, bathrooms, break rooms, security areas, elevator shafts, and stairwells. Loading dock areas located outside the walls of the building should not be included in the gross square footage.
| High Performance Energy | [14 empty] | Gov (Courthouse) | [6 empty] | Gov (Courthouse) | [5 empty] | Courthouse refers to buildings used for federal, state, or local courts, and associated administrative office space. Gross Floor Area should include all space within the building(s), including temporary holding cells, chambers, kitchens used by staff, lobbies, atriums, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
[16 empty] | Gov (Fire Station) | [6 empty] | Gov (Fire Station) | [5 empty] | Fire Station refers to buildings used to provide emergency response services associated with fires. Fire stations may be staffed by either volunteer or full-time paid firemen. Gross Floor Area should include all space within the building(s), including office areas, vehicle storage areas, residential areas (if applicable), storage areas, break rooms, kitchens, elevator shafts, and stairwells.
| N/A | [14 empty] | Gov (Library) | [6 empty] | Gov (Library) | [5 empty] | Library refers to buildings used to store and manage collections of literary and artistic materials such as books, periodicals, newspapers, films, etc. that can be used for reference or lending. Gross Floor Area should include all space within the building(s), including circulation rooms, storage areas, reading/study rooms, administrative space, kitchens used by staff, lobbies, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Ground Source Heat Pump | [14 empty] | Gov (Police Station) | [6 empty] | Gov (Police Station) | [5 empty] | Police Station applies to buildings used for federal, state, or local police forces and their associated office space. Gross Floor Area should include all space within the building(s), including offices, temporary holding cells, kitchens used by staff, lobbies, atriums, conference rooms and auditoriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Air Source Heat Pump | [14 empty] | Gov (Post Office) | [6 empty] | Gov (Post Office) | [5 empty] | Mailing Center/Post Office refers to buildings used as retail establishments dedicated to mail and mailing supplies. This includes U.S. Post Offices, in addition to private retailers that offer priority mail services and mailing supplies. Gross Floor Area should include all space within the building(s), including retail counters, administrative space, kitchens used by staff, lobbies, conference rooms, storage areas, stairways, and mechanical rooms.
| Waste Heat Recovery (All types) | [14 empty] | Gov (Prison) | [6 empty] | Gov (Prison) | [5 empty] | Prison/Incarceration refers to federal, state, local, or private-sector buildings used for the detention of persons awaiting trial or convicted of crimes. Gross Floor Area should include all space within the building(s), including holding cells, cafeterias, administrative spaces, kitchens, lobbies, atriums, conference rooms and auditoriums, fitness areas, storage areas, stairways, and elevator shafts.
[16 empty] | Hotel | [6 empty] | Hotel | [5 empty] | Hotel refers to buildings renting overnight accommodations on a room/suite and nightly basis, and typically include a bath/shower and other facilities in guest rooms. Hotel properties typically have daily services available to guests including housekeeping/laundry and a front desk/concierge. Hotel does not apply to properties where more than 50% of the floor area is occupied by fractional ownership units such as condominiums or vacation timeshares, or to private residences that are rented out on a daily or weekly basis. Hotel properties should be majority-owned by a single entity and have rooms available on a nightly basis. Condominiums or Time Shares should select the Multifamily Housing property use. Gross Floor Area should include all interior space within the building(s), including guestrooms, halls, lobbies, atriums food preparation and restaurant space, conference and banquet space, fitness centers/spas, indoor pool areas, laundry facilities, elevator shafts, stairways, mechanical rooms, storage areas, employee break rooms, and back-of-house offices.
[16 empty] | Laboratory | [6 empty] | Laboratory | [5 empty] | Laboratory refers to buildings that provide controlled conditions in which scientific research, measurement, and experiments are performed or practical science is taught. Gross Floor Area should include all space within the building(s) including workstations/hoods, offices, conference rooms, storage areas, decontamination rooms, mechanical rooms, elevator shafts, and stairwells.
[16 empty] | Manuf/Indust Plant | [6 empty] | Manuf/Indust Plant | [5 empty] | Manufacturing/Industrial Plant refers to buildings used for manufacturing or assembling goods. Typically a Manufacturing/Industrial plant includes a main production area that has high-ceilings and contains heavy equipment used for assembly line production. Gross Floor Area should include all space within the building(s) at the plant, including production areas, offices, conference rooms, employee break rooms, storage areas, mechanical rooms, stairways, and elevator shafts.
[16 empty] | Medical (Amb Surg Ctr) | [6 empty] | Medical (Amb Surg Ctr) | [5 empty] | Ambulatory Surgery Centers refers to health care facilities that provide same-day surgical care, including diagnostic and preventive procedures. Gross Floor Area should include all space within the building(s) including offices, operating and recovery rooms, waiting rooms, employee break rooms and kitchens, elevator shafts, stairways, mechanical rooms, and storage areas.
| Applicability | [14 empty] | Medical (Clinic/Emerg) | [6 empty] | Medical (Clinic/Emerg) | [5 empty] | Urgent Care Center/Clinic/Other Outpatient Office refers to buildings used to treat patients, usually on an unscheduled, walk-in basis, who have an injury or illness that requires immediate care but is not serious enough to warrant a visit to an emergency department. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
[16 empty] | Medical (Hospital) | [6 empty] | Medical (Hospital) | [5 empty] | Hospital refers to a general medical and surgical hospital (including critical access hospitals and children’s hospitals). These facilities provide acute care services intended to treat patients for short periods of time, including emergency medical care, physician's office services, diagnostic care, ambulatory care, surgical care, and limited specialty services such as rehabilitation and cancer care. The definition of Hospital accounts for all space types owned by the hospital that are located within the Hospital building/campus, including non-clinical spaces such as administrative offices, food service, retail, hotels, and power plant. Gross Floor Area should include all space within the building(s) on the campus including operating rooms, bedrooms, emergency treatment areas, medical offices, exam rooms, laboratories, lobbies, atriums, cafeterias, rest rooms, stairways, corridors connecting buildings, storage areas, and elevator shafts. More than 50% of the gross floor area of all buildings must be used for general medical and surgical services and more than 50% of the licensed beds must provide acute care services. Properties that use more than 50% of the gross floor area for long-term care (including long-term acute care), skilled nursing, specialty care, and/or ambulatory surgical centers or that have less than 50% of their beds licensed for acute care services are not eligible for an ENERGY STAR score. If your facility does not meet this definition, it is not eligible for an ENERGY STAR score as Hospital. You can choose from the other available healthcare property types: Ambulatory Surgical Center, Medical Office, Other/Specialty Hospital, Outpatient Rehabilitation/Physical Therapy, Urgent Care/Clinic/Other Outpatient, or Senior Care Community.
| Yes |  | Applies | [12 empty] | Medical (PT/Rehab) | [6 empty] | Medical (PT/Rehab) | [5 empty] | Outpatient Rehabilitation/Physical Therapy offices refers to buildings used to provide diagnosis and treatment for rehabilitation and physical therapy. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, indoor pool areas, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
| No |  | N/A | [12 empty] | Medical (Vet Office) | [6 empty] | Medical (Vet Office) | [5 empty] | A Veterinary Office refers to buildings used for the medical care and treatment of animals. Gross Floor Area should include all space within the building(s) including offices, exam rooms, waiting rooms, atriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
[16 empty] | Medical Office | [6 empty] | Medical Office | [5 empty] | Medical Office refers to buildings used to provide diagnosis and treatment for medical, dental, or psychiatric outpatient care. Gross Floor Area should include all space within the building(s) including offices, exam rooms, laboratories, lobbies, atriums, conference rooms and auditoriums, employee break rooms and kitchens, rest rooms, elevator shafts, stairways, mechanical rooms, and storage areas.
| Base Building's N/E status | [14 empty] | Office | [6 empty] | Office | [5 empty] | Office refers to buildings used for the conduct of commercial or governmental business activities. This includes administrative and professional offices. Gross Floor Area should include all space within the building(s) including offices, conference rooms and auditoriums, kitchens used by staff, lobbies, fitness areas for staff, storage areas, stairways, and elevator shafts.
[16 empty] | Office (Financial) | [6 empty] | Office (Financial) | [5 empty] | Financial Office refers to buildings used for financial services such as bank headquarters and securities and brokerage firms. Gross Floor Area should include all space within the building(s) including offices, trading floors, conference rooms and auditoriums, vaults, kitchens used by staff, lobbies, atriums, fitness areas for staff, storage areas, stairways, and elevator shafts.
| Connected to N/E System | [14 empty] | Other | [6 empty] | Other | [5 empty] | "Other" refers to buildings that do not fall within the available property use categories in Portfolio Manager. Before selecting Other, it is highly recommended that you review the full list of property uses available for selection to ensure that there is not a suitable category for your property. Gross Floor Area should include all space within the building(s), including space devoted to your main business activity, administrative offices, employee break rooms, bathrooms, stairways, and elevator shafts.
| Not Connected to N/E System | [14 empty] | Other (Education) | [6 empty] | Other (Education) | [5 empty] | Other – Education refers to buildings used for religious, community, or other educational purposes not described in the available property uses in Portfolio Manager (i.e educational purposes other than adult education, college/university, K-12 school, pre-school/daycare and vocational schools). Gross Floor Area should include all space within the building(s), including classrooms, administrative space, conference rooms, kitchens used by staff, lobbies, cafeterias, auditoriums, laboratory classrooms, stairways, elevator shafts, and storage areas.
| N/A | [14 empty] | Other (Entertainment) | [6 empty] | Other (Entertainment) | [5 empty] | Other - Entertainment/Public Assembly refers to buildings whose primary use is for entertainment or public gatherings and that do not meet the definition of any other property use defined in Portfolio Manager. Gross floor area should include all space within the building(s), including entertainment areas, administrative areas, and supporting areas such as storage rooms, hallways, restrooms, stairways, and maintenance areas.
[16 empty] | Other (Lodging/Res) | [6 empty] | Other (Lodging/Res) | [5 empty] | Other – Lodging/Residential refers to buildings used for residential purposes other than multifamily residential, single family home, senior care community, residence hall/dormitory, barracks, prison/incarceration, or hotel. Gross Floor Area should include all space within the building(s), including living areas, common areas, administrative space, kitchens used by staff, lobbies, waiting areas, cafeterias, stairways, atriums, elevator shafts, and storage areas.
[16 empty] | Other (Mall) | [6 empty] | Other (Mall) | [5 empty] | Other - Mall refers to buildings containing a collection of stores whose purpose is the sale of goods, but which do not fit into the enclosed mall, lifestyle center, or strip mall property types. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, storage areas, staff break rooms, walkways, stairwells, and mechanical areas.
[16 empty] | Other (Public Services) | [6 empty] | Other (Public Services) | [5 empty] | Other – Public Services refers to buildings used by public-sector organizations to provide public services other than those described in the available property uses in Portfolio Manager (i.e. services other than offices, courthouses, drinking water treatment and distribution plants, fire stations, libraries, mailing centers or post offices, police stations, prisons or incarceration facilities, social or meeting halls, transportation terminals or stations, or wastewater treatment plants). Gross Floor Area should include all space within the building(s), including administrative space, kitchens used by staff, lobbies, waiting areas, cafeterias, stairways, atriums, elevator shafts, landscaping sheds, and storage areas.
| Neighbourhood Energy Systems | [14 empty] | Other (Recreation) | [6 empty] | Other (Recreation) | [5 empty] | Other - Recreation refers to buildings primarily used for recreation that do not meet the definition of any other property use defined in Portfolio Manager. Gross Floor Area should include all space within the building(s), including recreational areas and supporting activities such as mechanical rooms, storage areas, elevator shafts, and stairwells.
[16 empty] | Other (Rest/Bar) | [6 empty] | Other (Rest/Bar) | [5 empty] | Other – Restaurant/Bar refers to buildings used for preparation and sale of ready-to-eat food and beverages, but which does not fit into the fast food restaurant, restaurant, or bar/nightclub property types. Gross Floor Area should include all space within the building(s), including kitchens, sales areas, dining areas, staff break rooms, and storage areas. Gross Floor Area should not include any outdoor/exterior seating areas, but the energy use of these outdoor areas should be reported on your energy meters.
[16 empty] | Other (Services) | [6 empty] | Other (Services) | [5 empty] | Other - Services refers to buildings in which primarily services are offered, but which does not fit into the Personal Services or Repair Services property types. Examples include kennels, photo processing shops, etc. Gross Floor Area should include all space within the building(s), including sales floors, offices, storage areas, staff break rooms, walkways, and stairwells.
| Choose One | [14 empty] | Other (Specialty Hosp) | [6 empty] | Other (Specialty Hosp) | [5 empty] | Other/Specialty Hospitals refers to long-term acute care hospitals, inpatient rehabilitation facilities, including Cancer Centers and Psychiatric and Substance Abuse Hospitals/Facilities. Gross Floor Area should include all space within the building(s) on the campus including: medical offices, patient rooms, laboratories, lobbies, atriums, cafeterias, rest rooms, stairways, corridors connecting buildings, storage areas, elevator shafts.
| N/A | [14 empty] | Other (Stadium) | [6 empty] | Other (Stadium) | [5 empty] | Other - Stadium refers to buildings primarily used for sporting events that do not meet the definition of any other property use defined in Portfolio Manager. Gross Floor Area should include all space within the building(s), including areas for athletic activity and spectator seating and supporting activities such as mechanical rooms, storage areas, elevator shafts, and stairwells.
| Creative Energy (Central Heat) N/E system | [14 empty] | Other (Tech) | [6 empty] | Other (Tech) | [5 empty] | Other – Technology/Science refers to buildings used for science and technology related services other than Laboratories and Data Centers. Gross Floor Area should include all space within the building(s), including areas with the main business activity, production areas, administrative offices, employee break areas, stairways, atriums, elevator shafts, and storage areas.
| City Owned False Creek NEU Service Area | [14 empty] | Other (Utility) | [6 empty] | Other (Utility) | [5 empty] | Other – Utility applies to buildings used by a utility for some purpose other than general office or energy/power generation. This may include utility transfer stations or maintenance facilities. Note that an administrative office occupied by a utility should be entered as Office, and a power or energy generation plant should be entered as Energy/Power Station. Gross Floor Area should include all space within the building(s), including administrative space, maintenance and equipment areas, generator rooms, kitchens used by staff, lobbies, meeting rooms, stairways, elevator shafts, and storage areas. This should not include any exterior spaces associated with utility operations.
| East Fraserlands (River District) N/E system | [14 empty] | Parking | [6 empty] | Parking | [5 empty] | Parking refers to buildings and lots used for parking vehicles. This includes open parking lots, parking structures that may be only partially enclosed, and fully-enclosed (or underground) parking structures. Parking structures may be free standing or may be physically connected to another building.
| Total site of 8,000 m2 or greater | [14 empty] | Personal Services | [6 empty] | Personal Services | [5 empty] | Personal Services refers to buildings used to sell services rather than physical goods. Examples include dry cleaners, salons, spas, etc. Gross Floor Area should include all space within the building(s), including sales floors, offices, storage areas, staff break rooms, walkways, and stairwells.
| Total new development of 45,000 m2 or greater | [14 empty] | Rec (Aquarium) | [6 empty] | Rec (Aquarium) | [5 empty] | Aquarium refers to buildings used to provide aquatic habitat primarily to live animals and which may include public or private viewing areas and educational programs. Gross Floor area should include public and restricted areas such as visitor walkways, tank space, retail areas, restaurants, laboratories, classrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Areas not in enclosed buildings, such as outdoor habitats, open-air theaters, walkways, and landscaped areas should not be included in the Gross Floor Area.
[16 empty] | Rec (Arena - indoor) | [6 empty] | Rec (Arena - indoor) | [5 empty] | Indoor Arena refers to enclosed structures used for professional or collegiate sports and entertainment events. Examples of events held in indoor arenas include basketball and hockey games, circus performances, and concerts. Indoor Arenas usually have capacities of 5,000 seats or more and are often characterized by multiple concourses and concession areas.
[16 empty] | Rec (Bar/Nightclub) | [6 empty] | Rec (Bar/Nightclub) | [5 empty] | Bar/Nightclub refers to buildings used primarily for social/entertainment purposes, and is characterized by most of the revenue being generated from the sale of beverages instead of food. Gross Floor Area should include all space within the building(s), including standing/seating areas, stage/dressing room areas, food/drink preparation or kitchen areas, retail areas, bathrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Properties whose primary business revenues are generated from the sale of food should be entered using one of the Restaurant property uses, even if there is a bar.
[16 empty] | Rec (Bowling Alley) | [6 empty] | Rec (Bowling Alley) | [5 empty] | Bowling alley refers to buildings used for public or private, recreational or professional bowling. Gross Floor Area should include all space within the building(s), including bowling lanes, concession areas, party rooms, retail areas, administrative/office space, employee break rooms, storage areas, and mechanical rooms.
[16 empty] | Rec (Casino) | [6 empty] | Rec (Casino) | [5 empty] | Casino refers to buildings primarily used to conduct gambling activities including both electronic and live table games. Gross Floor Area should include all space within the building(s), including the main casino floor/gaming area, restaurants/bars, retail areas, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. If your Casino is located in the same building as a hotel, we recommend that you enter a separate hotel property use.
[16 empty] | Rec (Fitness Ctr/Gym) | [6 empty] | Rec (Fitness Ctr/Gym) | [5 empty] | Fitness Center/Health Club/Gym refers to buildings used for recreational or professional athletic training and related activities. Gross Floor Area should include all space within the building(s), including weight and cardio equipment areas, personal training areas, courts, locker rooms, sauna and spa areas, retail areas, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
[16 empty] | Rec (Ice/Curling Rink) | [6 empty] | Rec (Ice/Curling Rink) | [5 empty] | Ice/Curling Rink refers to buildings that include one or more ice sheets used for public or private, recreational or professional skating, curling, hockey, or other similar activities. Gross Floor Area should include all space within the building(s), including ice area, spectator areas, concession stands, retail areas, locker rooms, administrative/office areas, employee break rooms, mechanical rooms, and storage areas. Larger facilities primarily serving professional or collegiate functions and with significant spectator seating should review the definition for Indoor Arena to determine the best classification.
| Renewable & HP Energies | [14 empty] | Rec (Movie Theatre) | [6 empty] | Rec (Movie Theatre) | [5 empty] | Movie theater refers to buildings used for public or private film screenings. Gross Floor Area should include all space within the building(s), including seating areas, lobbies, concession stands, bathrooms, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
[16 empty] | Rec (Museum) | [6 empty] | Rec (Museum) | [5 empty] | Museum refers to buildings that display collections to outside visitors for public viewing and enjoyment and for informational/educational purposes. Gross Floor Area should include all space within the building(s), including public collection display areas, meeting rooms, classrooms, gift shops, food service areas, administrative/office space, mechanical rooms, storage areas for collections, elevator shafts, and stairwells.
| Photovoltaic systems | [14 empty] | Rec (Performing Arts) | [6 empty] | Rec (Performing Arts) | [5 empty] | Performing Arts refers to buildings used for public or private artistic or musical performances. Gross Floor Area should include all space within the building(s), including seating, stage and backstage areas, food service areas, retail areas, rehearsal studios, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
| Solar Thermal systems | [14 empty] | Rec (Race Track) | [6 empty] | Rec (Race Track) | [5 empty] | Race Track refers to buildings used primarily to hold racing events such as vehicle races, track/field races, horse races, and/or dog-races. Gross Floor Area should include all spectator viewing areas, concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the race track itself should also be included in the gross floor area, along with the footprint of any staging areas.
| Bio-fuel based energy | [14 empty] | Rec (Roller Rink) | [6 empty] | Rec (Roller Rink) | [5 empty] | Roller Rink refers to buildings used primarily for roller-skating, inline skating/rollerblading, or skateboarding. Gross Floor Area should include all space within the building(s), including the rink space, concession areas, locker rooms, retail areas, administrative/office areas, employee break rooms, mechanical rooms, and storage areas.
| Geothermal Heating | [14 empty] | Rec (Social/Mtg Hall) | [6 empty] | Rec (Social/Mtg Hall) | [5 empty] | Social/Meeting hall refers to buildings primarily used for public or private gatherings. This may include community group meetings, seminars, workshops, or performances. Please note that there is another property use available, Convention Center, for large exhibition and conference facilities. Gross Floor Area should include all space within the building(s), including meeting rooms, auditoriums, food service areas, lobbies, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells.
| Geothermal Electric | [14 empty] | Rec (Stadium - closed) | [6 empty] | Rec (Stadium - closed) | [5 empty] | Stadium (Closed) refers to structures with a permanent or retractable roof which are used primarily for professional or collegiate sports and entertainment events. Examples of events held in closed stadiums include baseball and football games, and concerts. Closed Stadiums usually have capacities of 25,000 seats or more and are often characterized by multiple concourses and concession areas. Gross Floor Area should include all space within the building(s), including concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the playing field should also be included in the gross floor area.
| Ground Source Heat Pump | [14 empty] | Rec (Stadium - open) | [6 empty] | Rec (Stadium - open) | [5 empty] | Stadium (Open) refers to structures used primarily for professional or collegiate sports and entertainment events in which the playing field is not covered and is exposed to the outside. Examples of events held in open stadiums include baseball, football, and soccer games, and concerts. Open Stadiums usually have capacities of 5,000 seats or more and are often characterized by multiple concourses and concession areas. Gross Floor Area should include all space within the building(s), including concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells. The footprint of the playing field should also be included in the gross floor area.
| Air Source Heat Pump | [14 empty] | Rec (Swimming Pool) | [6 empty] | Rec (Swimming Pool) | [5 empty] | Swimming Pool refers to any heated swimming pools located either inside or outside. To enter a swimming pool, a specific pool size must be selected. In order to enter buildings associated with a Swimming Pool, the main property use must be entered (e.g., K-12 School, Hotel, Fitness Center/Health Club/Gym, etc).
| Waste Heat Recovery (All types) | [14 empty] | Rec (Zoo) | [6 empty] | Rec (Zoo) | [5 empty] | Zoo refers to buildings used primarily to provide habitat to live animals and which may include public or private viewing and educational programs. Gross Floor Area should include all space within all fully enclosed buildings, including, habitats, visitor viewing areas, theaters, classrooms, food service areas, retail stores, veterinary offices, exhibit space, administrative/office space, mechanical rooms, storage areas, elevator shafts, and stairwells. Areas not in fully enclosed buildings, such as outdoor habitats, open-air theaters, walkways, and landscaped areas should not be included in the Gross Floor Area.
[16 empty] | Residential (Barracks) | [6 empty] | Residential (Barracks) | [5 empty] | Barracks refers to residential buildings associated with military facilities or educational institutions which offer multiple accommodations for long-term residents. Gross Floor Area should include all space within the building(s), including bedrooms, common areas, food service facilities, laundry facilities, meeting spaces, exercise rooms, health club/spas, lobbies, elevator shafts, storage areas, and stairways.
[16 empty] | Residential (Hall/Dorm) | [6 empty] | Residential (Hall/Dorm) | [5 empty] | Residence Hall/Dormitory refers to buildings associated with educational institutions or military facilities which offer multiple accommodations for long-term residents. Gross Floor Area should include all space within the building(s), including bedrooms, common areas, food service facilities, laundry facilities, meeting spaces, exercise rooms, health club/spas, lobbies, elevator shafts, storage areas, and stairways.
[16 empty] | Res (Multifamily-Common Areas) | [6 empty] | Res (Multifamily-Common Areas) | [5 empty] | Multifamily-Common Areas refers only to the common areas of residential buildings that contain more than two residential living units. These properties may be high rise buildings (4 or more stories), or mixed use buildings of 3 stories or less. Occupants of these buildings may include tenants, cooperators, and/or individual owners. IMPORTANT: Work done on the building's envelope is considered base building work and should use this checklist. For work done within residential suites, applicants are to use the Alterations to Residential Suites checklist.
[16 empty] | Residential (Senior Care) | [6 empty] | Residential (Senior Care) | [5 empty] | Senior Care Community refers to buildings that house and provide care and assistance for elderly residents. Gross Floor Area should include all space within the building(s) including individual rooms or units, wellness centers, exam rooms, community rooms, small shops or service areas for residents and visitors (e.g. hair salons, convenience stores), staff offices, lobbies, atriums, cafeterias, kitchens, storage areas, hallways, basements, stairways, corridors between buildings, and elevator shafts. The ENERGY STAR score for Senior Care community applies to nursing homes (skilled nursing facilities) and assisted living facilities. Independent senior living communities are not eligible. However, it is common for some Senior Care Communities to offer a mix of residential options including independent living, assisted living, and skilled nursing. More than 50% of the units in a community must be considered skilled nursing and/or assisted living in order to be eligible for an ENERGY STAR score as a Senior Care Facility. One exception to this rule is for communities in which 50% or more of the units are independent living (IL) but the IL buildings are separately metered stand-alone buildings, a valid rating can be generated only by fully excluding the IL buildings from the rest of the campus. Facilities with more than 50% independent living units cannot earn an ENERGY STAR score and should benchmark using the Multifamily property type.
[16 empty] | Retail | [6 empty] | Retail | [5 empty] | Retail Store refers to individual stores used to conduct the retail sale of non-food consumer goods such as clothing, books, toys, sporting goods, office supplies, hardware, and electronics. Buildings containing multiple stores should be classified as enclosed mall, lifestyle center, or strip mall. Gross Floor Area should include all space within the building(s), including sales areas, storage areas, offices staff break rooms, elevators, and stairwells. To receive an ENERGY STAR score, a Retail Store must be asingle store that is at least 5,000 square feet and has an exterior entrance to the public. The ENERGY STAR score applies to: Department Stores, Discount Stores, Supercenters, Warehouse Clubs, Drug Stores, Dollar Stores, Home Center/Hardware Stores, and Apparel/Specialty Stores (e.g. books, clothing, office products, toys, home goods, and electronics). Eligible store configurations include: free standing stores; stores located in open air or strip centers (a collection of attached stores with common areas that are not enclosed); and mall anchors. Retail configurations not eligible to receive an ENERGY STAR score include: enclosed malls; individual stores located within enclosed malls; lifestyle centers; strip malls; and individual stores that are part of a larger non- mall building (i.e. office or hotel). Convenience Stores, Automobile Dealerships, and Restaurants are not eligible to earn an ENERGY STAR score as Retail. Supermarkets are eligible for an ENERGY STAR score under the Supermarket property type. Note: In order to be eligible to earn ENERGY STAR certification, your building must be located in the US or its territories, or owned by the US government outside of the US.
[16 empty] | Retail (Auto Dealership) | [6 empty] | Retail (Auto Dealership) | [5 empty] | Automobile Dealership refers to buildings used for the sale of new or used cars and light trucks. Gross Floor Area should include all space within the building(s), including sales floors, offices, conference rooms, vehicle service centers, parts storage areas, waiting rooms, staff break rooms, hallways, and stairwells. Gross Floor Area should not include any exterior spaces such as vehicle parking areas.
[16 empty] | Retail (Conv w Gas Stn) | [6 empty] | Retail (Conv w Gas Stn) | [5 empty] | Convenience Store with Gas Station refers to buildings that are co-located with gas stations and are used for the sale of a limited range of items such as groceries, toiletries, newspapers, soft drinks, tobacco products, and other everyday items. Convenience Store with Gas Station may include space for vehicle servicing and repair. Gross Floor Area should include all space within the building(s), including sales floors, offices, staff break rooms, storage areas, and vehicle repair areas. Energy use associated with outside areas such as vehicle parking and gas filling areas should be included with the total energy use for the building(s), but the square footage associated with these outdoor areas should not be included in the Gross Floor Area.
[16 empty] | Retail (Convenience St) | [6 empty] | Retail (Convenience St) | [5 empty] | Convenience Store without Gas Station refers to buildings used for the sale of a limited range of items such as groceries, toiletries, newspapers, soft drinks, tobacco products, and other everyday items, which are not co-located with a gas station. Gross Floor Area should include all space within the building(s), including sales floors, offices, staff break rooms, and storage areas. Conference facilities located within a Hotel should be included along with your Hotel property use details, rather than added as a separate Convention Center property use. Conference facilities primarily serving smaller meetings should be entered as Social/Meeting Hall.
[16 empty] | Retail (Lifestyle Ctr) | [6 empty] | Retail (Lifestyle Ctr) | [5 empty] | Lifestyle Center refers to a mixed use commercial development that includes retail stores and leisure amenities, where individual retail stores typically contain an entrance accessible from the outside and are not connected by internal walkways. Lifestyle centers have an open air design, unlike traditional enclosed malls, and often include landscaped pedestrian areas, as well as streets and vehicle parking. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, residential areas, storage areas, staff break rooms, walkways, stairwells, and mechanical areas. Do not include any exterior spaces such as pedestrian walkways or vehicle parking areas.
[16 empty] | Retail (Mall - enclosed) | [6 empty] | Retail (Mall - enclosed) | [5 empty] | Enclosed Mall refers to buildings that house multiple stores, often “anchored” by one or more department stores, and with interior walkways. Most stores will not have entrances accessible from outside, with the exception of the “anchor” stores. Gross Floor Area should include all space within the building(s), including retail stores, offices, food courts, restaurants, storage areas, staff break rooms, atriums, walkways, stairwells, and mechanical rooms.
[16 empty] | Retail (Repair: Car/Shoe) | [6 empty] | Retail (Repair: Car/Shoe) | [5 empty] | Repair Services refers to buildings in which some type of repair service is provided. Examples include vehicle service or repair shops, shoe repair, jewelry repair, locksmiths, etc. Gross Floor Area should include all space within the building(s), including sales floors, repair areas, workshops, offices, parts storage areas, waiting rooms, staff break rooms, hallways, and stairwells.
[16 empty] | Retail (Strip Mall) | [6 empty] | Retail (Strip Mall) | [5 empty] | Strip mall refers to buildings comprising more than one retail store, restaurant, or other business, in an open-air configuration where each establishment has an exterior entrance to the public and there are no internal walkways. Gross Floor Area should include all space within the building(s), including retail stores, offices, restaurants, storage areas, staff break rooms, and stairwells. Do not include any exterior spaces such as vehicle parking areas. Note that individual stores within strip malls may be eligible to receive an ENERGY STAR score if they are over 5,000 square feet in size and have an exterior entrance to the public.
[16 empty] | Retail (Supermkt/Groc) | [6 empty] | Retail (Supermkt/Groc) | [5 empty] | Supermarket/Grocery Store refers to buildings used for the retail sale of primarily food and beverage products, and which may include small amounts of preparation and sale of ready-to-eat food. Buildings where the primary business is the on-site preparation and sale of ready-to-eat food should use one of the Restaurant property types. Gross Floor Area should include all space within the building(s), including the sales floor, offices, storage areas, kitchens, staff break rooms, and stairwells. Gross Floor Area should include all space within the building, including court/rink space, all concourse space on which workers or guests can walk, concession areas, retail stores, restaurants, administrative/office areas, employee break rooms, kitchens, mechanical rooms, storage areas, elevator shafts, and stairwells.
[16 empty] | Retail (Wholesale Club) | [6 empty] | Retail (Wholesale Club) | [5 empty] | Wholesale Club/Supercenter refers to buildings used to conduct the retail sale of a wide variety of merchandise, typically in bulk quantities. Merchandise may include food, clothing, office supplies, furniture, electronics, books, sporting goods, toys, and hardware. Gross Floor Area should include all space within the building(s), including the sales floor, offices, storage areas, kitchens, staff break rooms, elevators, and stairwells.
[16 empty] | Self Storage Facility | [6 empty] | Self Storage Facility | [5 empty] | Self-Storage Facility refers to buildings that are used for private storage. Typically, a single Self Storage Facility will contain a variety of individual units that are rented out for the purpose of storing personal belongings. Gross Floor Area should include all space within the building(s), including individual storage units, administrative offices, security and maintenance areas, mechanical rooms, hallways, stairways, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[16 empty] | Trans Terminal/Station | [6 empty] | Trans Terminal/Station | [5 empty] | Transportation Terminal/Station applies to buildings used primarily for accessing public or private transportation. This includes train stations, bus stations, airports, and seaports. These terminals include areas for ticket purchases, and embarkation/disembarkation, and may also include public waiting areas with restaurants and other concessions. Gross Floor Area should include all space within the building(s), including boarding areas, waiting areas, administrative space, kitchens used by staff, lobbies, restaurants, cafeterias, stairways, atria, elevator shafts, and storage areas. This should not includeany exterior spaces associated with the terminals, such as drop-off areas, outdoor platforms, or outdoor loading docks/bays.
[16 empty] | Unknown (Core & Shell) | [6 empty] | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
[16 empty] | Warehouse (Non-Refrig) | [6 empty] | Warehouse (Non-Refrig) | [5 empty] | Non-Refrigerated Warehouse refers to unrefrigerated buildings that are used to store goods, manufactured products, merchandise or raw materials. Gross Floor Area should include all space within the building(s), including the main storage rooms, administrative office offices, lobbies, stairways, restrooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[16 empty] | Warehouse (Refrig) | [6 empty] | Warehouse (Refrig) | [5 empty] | Refrigerated Warehouse refers to refrigerated buildings that are used to store perishable goods or merchandise under refrigeration at temperatures below 50 degrees Fahrenheit. Gross Floor Area should include all space within the building(s), which includes temperature-controlled areas, administrative offices, lobbies, stairways, restrooms, equipment storage areas, and elevator shafts. This should not include exterior/outdoor loading bays or docks.
[16 empty] | Worship Facility | [6 empty] | Worship Facility | [5 empty] | Worship Facility refers to buildings that are used as places of worship. This includes churches, temples, mosques, synagogues, meetinghouses, or any other buildings that primarily function as a place of religious worship. Gross Floor Area should include all areas inside the building that includes the primary worship area, including food preparation, community rooms, classrooms, and supporting areas such as restrooms, storage areas, hallways, and elevator shafts. The ENERGY STAR score for Worship Facilities applies to buildings that function as the primary place of worship and not to other buildings that may be associated with a religious organization, such as living quarters, schools, or buildings used primarily for other community activities. To receive an ENERGY STAR score, a Worship facility must have at least 25 seats, but cannot have more than 4,000.
[16 empty] | Unknown (Core & Shell) | [6 empty] | Unknown (Core & Shell) | [5 empty] | Use this designation if interior space design is not part of this scope of work. To be defined during TI (Tenant Improvement) design stage.
| NECB Section | [10 empty] | NECB Section
| Admin | [10 empty] | Entire Energy Package (checklist + all supporting docs)
| Building Envelope | [10 empty] | Admin - Checklist
| Lighting | [10 empty] | Building Envelope Compliance
| HVAC | [10 empty] | Lighting Compliance
| Service Water Heating | [10 empty] | HVAC Compliance
Service Water Heating Compliance
Note on B3: Insert the building's main address on this line. If your space is within the main building then also indicate the unit or suite number if any. For buildings with multiple commercial spaces, each having unique addresses, insert the building's main address here then the specific commercial space's address on the next row below.
Note on B4: If your space is a retail or commercial unit within a building, and your space has a different address from the main building, then put the building's address on the row above and the address of the retail or commercial unit on this row, starting with a unit number if any.
Note on C13: Most spaces have only one use. If more than one use then indicate all space uses. If more than one space or tenancy, then indicate uses, if more than one. Example: If a single tenancy (office) is becoming two tenancies (Retail, and Medical Office) then indicate based on size, with Primary being largest tenancy.
Note on C25: Do not include the City neighbourhood energy systems here. See below for declaration of City neighbourhood energy systems.
Note on D39: If building a complete wall or a complete roof, then comply with NECB 2015 envelope requirements and use envelope forms provided in the Building Envelpe tab. If only doing partial work or cladding work etc then submit only the Calculator to show that the envelope performance has not been made worse.
Note on D69: Choose the necessary area of revision (Env, Lighting, HVAC, SWH) here, then the associated revised document for resubmission, on the same row, in the column to the right.
Note on H3: Insert the suite or unit number if your space uses the address of the main building, otherwise leave blank.
Note on H4: Insert the suite number, if any, of your commercial space, otherwise leave blank.
Note on H13: Indicate Usage(s) starting with largest area, then add in order of decreasing area.
Note on H16: Use this cell to see a detailed description of the building(s) being considered above. To see the description, first choose the building from the drop box in this cell. The detailed description of the selected building will appear outside the checklist, to the right.
Note on I20: If not applicable, indicate "N/A". Indicate EUI requirement per the Rezoning Conditions.
Note on I21: If not applicable, indicate "N/A". Indicate EUI achieved per the modeling output (ECB).
Note on J28: If the existing building is already tied into an N/E system then choose the "Connected…" option. If within an N/E area but the building is not connected to the N/E system then choose the "Not Connected…" option. If the building is not within an N/E area then choose the "N/A" option.
Note on K3: Insert Building number.
Note on K4: Insert Tenancy number.
Note on N35: Answer "Yes" if your scope of work on the building envelope includes the addition, deletion or replacement of glazing, skylights, doors, or insulation. If you are only refurbishing then reinstalling the original components then answer "No".
Note on N41: If you are adding lighting load, answer "Yes". If you are altering luminaires (replacing, removing, or relocating from one space into another) then answer "Yes", otherwise answer "No".
Note on N47: If you are adding any HVAC equipment (including kitchen exhaust and make-up air systems) that has an energy component such as motors ( >1 hp ), burners, coils, or heat exchangers, then answer "Yes". If you are only repairing existing equipment or moving diffuser locations then answer "No".
Note on N55: If you are adding any Service Water Heating equipment (boilers, hot water heater, on-demand system) that has an energy component such as motors, burners, coils, or heat exchangers, then answer "Yes". If you are only repairing or relocating existing equipment, then answer "No".
Note on O3: Insert building's street name by using drop box.
Note on O4: Insert tenancy's street name by using drop box.
Note on O13: Indicate area in square meters. Example: 3540 not 3540sqm.
Note on P35: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P41: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P47: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on P55: Indicate party responsible for "Yes" or "No" response. Include company name and name of individual.
Note on Q20: Input to first decimal, without % sign. Example: 20.0 Indicate the required energy cost savings (reduction) beyond 90.1-2010, as stipulated by the Rezoning Conditions. Note: Savings to be measured in % energy cost saved.
Note on Q21: Input to first decimal, without % sign. Example: 20.0 This cell indicates the energy cost improvement (reduction) achieved beyond 90.1-2010, by percentage. Note, this measures energy cost savings, not energy savings.
Note on S59: Indicate "X" if you are providing a water heating system that satisfies the requirements. Indicate "N/A" if a water heating system is not provided.
Note on T21: New Construction or Core & Shell
Note on Y51: Insert source of input per these examples: - ASHRAE 62 - 2001 (except Addendum n) or - ASHRAE 62.1 - 20__ etc
Note on Y53: Insert source of input per these examples: - Actual: Supplied by Owner or - ASHRAE 90.1 - 20__ Table or Chart # etc
Note on AB25: Indicate here any additional High Performance Energy system not listed within Drop-Down menu.
Note on AD24: Indicate here any additional Renewable Energy system not listed within Drop-Down menu.
Note on AE3: Submit without number, then update once permit number is known.
Note on AE20: Indicate level of LEED Certification required by Rezoning Conditions.
Note on AE21: Indicate level of LEED Certification achieved.
Note on AF13: Intent: Account for all conditioned non-Residential (commercial etc) spaces only. If area is zero or Not Applicable then input 0, not N/A or 0sqm. Space Area calculation: Calculate all areas except "non-conditioned" spaces. This means to exclude all outside spaces (patios), and include all interior spaces (ie storage, etc) as long as they are conditioned.
Note on AF14: If area is zero or Not Applicable then input 0, not N/A or 0 sqm. Intent: i) If scope includes Building Envelope work of a residential unit, use area of conditioned Residential space(s) only. ii) ASHRAE does not apply to areas within residential suites, just the common areas of residential buildings (and envelope per i above), therefore, indicate total area of common spaces being worked on. "Conditioned" Space Area calculation: Calculate all areas except "non-conditioned" spaces. This means to exclude all outside spaces (patios), and include all interior spaces (ie storage, etc) as long as they are conditioned.
Note on AF15: Intent: Account for all semiheated spaces only. If area is zero or Not Applicable then input 0, not N/A or 0sqm.
Note on AG16: Answer "Yes" if the entrance to the space is directly from the outdoors. Answer "No" if the entrance to the space is via another interior space such as a corridor or mall.
Note on AG17: Answer N/A if there is no outdoor entrance. Answer "Yes" if a new entrance is being built for the space, or if the existing outdoor entrance to the space is being modified. Answer "No" if the existing outdoor entrance to the space is not being modified.
Note on AG20: Indicate number of LEED energy pts (EAc1) required by Rezoning Conditions. If not specified, indicate N/A but still indicate number of pts achieved below.
Note on AG21: Indicate number of LEED energy pts (EAc1) achieved as shown on LEED Letter Template for EAc1.
Note on AG31: Are either architects or engineers involved in this project?
Note on AG33: Only Food and/or Beverage establishments are eligible for exterior patio heating systems.

## Building Envelope
Envelope for First TIs within NECB/ZEBP Buildings
Building Address: | [6 empty] | Building Permit Application #:
Tenant Address:
Designer of Rec: |  |  |  |  | Email: |  | Telephone:
Contact Person: |  |  |  |  | Email: |  | Telephone:
Reconstructed and Altered Opaque Assemblies
Assembly # / Tag |  | Assembly Type | Assembly Name / Description | Type of Alteration |  | Assembly USImax Value (W/(m2∙K))
[6 empty] | Existing | Design | Code or Allowable (USI / U)
Added and Altered Fenestration Assemblies
Building's vertical fenestration (Door or Glazing);
i) Door or Glazing is being repaired/replaced/added?
ii) N/A
iii) N/A
iv) N/A
Building's horizontal fenestration;
i) Skylight is being repaired/replaced/added?
ii) N/A
Assembly # |  | Assembly Type | Assembly Name / Description | Type of Alteration |  | Assembly USImax Value (W/(m2∙K))
[6 empty] | Existing | Design | Code or Max Allowable (USI / U)
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [6 empty] | Version: 250403-1
Opaque Assemblies (Walls, Roof, Door, Slab, Floor)
|  | Yes/No |  | Type of Alt |  |  | VLOOKUP Table
|  | Yes |  | Repair |  |  | Wall | 0.290 / 0.051
|  | No |  | New (replace) |  |  | Roof | 0.164 / 0.029
|  |  |  | New (add) |  |  | Floor | 0.193 / 0.033
[7 empty] | Wall (w grnd) | 0.568 / 0.100
[7 empty] | Roof (w grnd) | 0.568 / 0.100
[7 empty] | Slab | 0.757 / 0.133
[7 empty] | Door | 2.12 / 0.373
Fenestration (Glazing, Door, Skylight)
|  | If glazing < 40% | [5 empty] | If replacement < 25% | If replacement > 25%
|  |  | Glazing | Repair |  | Glazing-Repair |  | Match existing, or better |  | Match existing, or better
|  |  | Glazing | New (replace) |  | Glazing-New (replace) |  | Match existing, or better |  | 1.9 / 0.335
|  |  | Glazing | New (add) |  | Glazing-New (add) |  | 1.9 / 0.335 |  | 1.9 / 0.335
|  |  | Door | Repair |  | Door-Repair |  | Match existing, or better |  | Match existing, or better
|  |  | Door | New (replace) |  | Door-New (replace) |  | Match existing, or better |  | 2.12 / 0.373
|  |  | Door | New (add) |  | Door-New (add) |  | 2.12 / 0.373 |  | 2.12 / 0.373
|  |  | Skylight | Repair |  | Skylight-Repair |  | Match existing, or better
|  |  | Skylight | New (replace) |  | Skylight-New (replace) |  | Match existing, or better
|  |  | Skylight | New (add) |  | Skylight-New (add) |  | 2.69 / 0.473
If glazing > 40%
[6 empty] | Glazing | Repair | Match existing, or better |  | Match existing, or better
[7 empty] | New (replace) | Match existing, or better |  | Match existing, or better
[7 empty] | New (add) | Trade-off |  | Trade-off
[6 empty] | Door | Repair | Match existing, or better |  | Match existing, or better
[7 empty] | New (replace) | Match existing, or better |  | Match existing, or better
[7 empty] | New (add) | Trade-off |  | Trade-off
|  | Skylight | [5 empty] | If skylight < 2% | If 2% > skylight < 5% |  | If skylight > 2%
|  |  | Skylight | Repair |  | Skylight-Repair |  | Match existing, or better |  | Match existing, or better | Match existing, or better
|  |  | Skylight | New (replace) |  | Skylight-New (replace) |  | Match existing, or better |  | 2.69 / 0.473 | 2.69 / 0.473
|  |  | Skylight | New (add) |  | Skylight-New (add) |  | 2.69 / 0.473 |  | 2.69 / 0.473 | Trade-off
Note on C37: Alteration rules per the NECB alteration language found within "Notes to Part 11" of the VBBL. See link.
Note on C41: Includes new skylights to be added.
Note on D43: Complete questions within Rows 33-41 before attempting to complete Fenestration Table below.
Note on F41: Ex: 1.7% to be indicated as 1.7
Note on I44: USI value for Repaired or replaced skylight assembly.
Note on J44: USI value for New or Repaired skylight assembly.

## Lighting
Lighting for First TIs within NECB/ZEBP Buildings
Building Address: | [6 empty] | Building Permit Application #:
Tenant Address:
Designer of Rec: |  |  |  | Email: |  |  | Telephone:
Contact Person: |  |  |  | Email: |  |  | Telephone:
Interior Space |  |  |  |  | Lighting Power (W) | LPD (W/ft2) |  | Applicable Controls |  | Code Allowable LP
ID # | Space Use |  | Area |  |  | Design | Code
| (see Table 4.2.1.6.) |  | (ft2)
|  |  | 0 |  | 0 |  |  |  | Version: 250403-1 | 0
Note on K47: Total Design LP divided by Total Area.
Note on L10: Adjusted to imperial W/sqft.
Note on L47: Total LP allowance divided by Total Area.

## HVAC Equip
HVAC Alterations for NECB/ZEBP Buildings
Building Address: | [5 empty] | Building Permit Application #:
Tenant Address:
Designer of Rec: |  |  |  | Email: |  | Telephone:
Contact Person: |  |  |  | Email: |  | Telephone:
Equipment # and Description | HVAC Equip Table # |  | Component or Equipment Type (Tables 5.2.12.1.- A through P) | Cooling / Heating Capacity (kW) | Rating Conditions | Equipment Performance (AFUE, CoP, EER, Et, SEER)
[6 empty] | Code (Table 5.2.12.1.) | Design
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
.
|  | vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [5 empty] | Version: 250425-1

## Service Water Htg
Service Water Heating for First TIs within NECB/ZEBP Buildings
Building Address: | [7 empty] | Bldg Permit Applic #:
Tenant Address:
Designer of Rec: |  |  |  | Email: |  |  |  | Telephone:
Contact Person: |  |  |  | Email: |  |  |  | Telephone:
Equip # and Description |  | Component or Equipment Type (see Table 6.2.2.1.) | Q Rated Input (kW) | Vr Rated Capacity (L) | Vs Tank Volume (L) | Q / Vs (W/L) | FHR Rating Cond | Equipment Performance |  |  | Summation of All Numeric Formulas + Text Results |  |  |  |  | 2 | Applicant Inputs |  |  |  | 3 | 4 | 5 |  | 6 | 7 |  | 8 | 9 |  | 10 | 11 |  | 12 | 13 |  | 14 |  | 15 |  | 16 | 17 | 18 |  | 19 | 20 |  | 21
[8 empty] | Code |  | Design | [5 empty] | Formula | Q | Vr | Vs | FHR |  | SL (top inlet) |  | Equation Result | SL (bottom inlet) |  | Equation Result | SL (top inlet) |  | Equation Result | SL (bottom inlet) |  | Equation Result | SL (w division) |  | Equation Result | EF | Equation Result | Et (& instant) | Equation Result | Et and SL (w Q & SqRt Vr) combo |  |  | Equation Result | UEF (w FHR and Vs) |  | Equation Result
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  |  | 0
| vancouver.ca/home-property-development/large-building-energy-requirements-forms-checklists.aspx | [7 empty] | Version: 250425-1

## Data Line 4 Data Mine! (hidden)
No. | Data Extracted from (Tab Name) | Version | Building Address | Tenant or CRU no. | TIPs Eligible? | BOMA BESt? | b/t 90.1-2010? | BP Application No. | Primary Use | Primary Use Area | Secondary Use | Secondary Use Area | Tertiary Use | Tertiary Use Area | Non-Res Space Area | Resid Space Area | Semiheated Space Area | Exterior Heated Patio or Space Area | Any Reg Proff on Project? | Voluntry Upgrade, Repair, Small Suite, Minor Renov, Major Renov, Change MOC, Alteration (Addition) |  |  | N/E System | Base Bldg's N/E Status | TI's Thermal Energy Reqmt | Bldg Env | HVAC | SWH | Power | Lighting | Exemption | Categories of Alterations |  |  | Option Chosen (Required) | Non-Menu Item Chosen (Required)
| Data Mining Admin |  | General Building Information | [16 empty] | Permit Type(s) |  |  | N Energy Systems |  |  | ASHRAE - Scope of Work |  |  |  |  | Energy Upgrade
| Energy Checklist - Alterations | 250425-1 |  | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 | List All Revised and Resubmitted Deliverables Using Drop-Down Boxes Below; | 0 | 0
Note on U1: Zahra Teshnizi: http://evaluebc.bcassessment.ca/